## Sheet1
Chapter and text
0 | Foreword
1
2 | 1 Scope
3 | 2 Normative references
4
5
6
7 | 3 Terms and definitions
8 | 4 Abbreviations
9
10
11
12 | 5 Management of technical safety
13 | 5.1 General
14 | requirements ISO 80079-36. Explosive atmospheres - Part 36: Non-electrical equipment for explosive atmospheres - Basic method and requirements IEC 60079(part 10, part 14:2013/COR1:2016 and part 29), Explosive atmospheres IEC 60331(all parts), Tests for electric cables under fire conditions Œ Circuit integrity IEC 61508(all parts), Functional safety of electrical/electronic/programmable electronic safety-related systems IEC 61511(all parts), Functional safety Œ Safety instrumented systems for the process industry sector IEC 61892(parts 1, 2, 3, 5, 6:2013 and 7) Mobile and fixed offshore units Œ Electrical installations API RP 14C:2017, Recommended Practice for Analysis, Design, Installation, and Testing of Basic Surface Safety Systems for Offshore Production Platforms (8th ed) API Spec 17J, Specification for Unbonded Flexible Pipe API STD 520, Sizing, Selection, and Installation of Pressure-relieving Devices API STD 521, Pressure-Relieving and Depressurizing Systems Directive 94/9/EC, Concerning equipment and protective systems intended for use in potentially explosive atmospheres (ATEX ﬁProductﬂ) DNVGL-ST-E406, Design of Free Fall Lifeboats DNVGL-ST-F201, Dynamic risers NORSOK S-001:2018 NORSOK © 2018 3 EEMUA 191 Alarm systems - a guide to design, management and procurement EI 15, Model code of safe practice Part 15: Area classification code for installations handling flammable fluids LSA Code, IMO SOLAS Life saving appliances (LSA) Code, adopted by the Maritime Safety Committee by resolution MSC.48 (66) Norwegian Oil and Gas Association GL064, Anbefalte retningslinjer for etablering av områdeberedskap Norwegian Oil and Gas Association GL070, Guidelines for the Application of IEC 61508 and IEC 61511 in the petroleum activities on the continental shelf Norwegian Oil and Gas Association GL075, Anbefalte retningslinjer for vannbaserte brannbekjempelsessystemer Norwegian Oil and Gas Association GL094, Kravspesifikasjoner for redningsdrakt til bruk på norsk kontinentalsokkel. MODU Code, Code for the construction and equipment of mobile offshore drilling units NFPA 11, Standard for Low-, Medium-, and High-Expansion Foam NFPA 13, Installation of Sprinkler Systems NFPA 14, Standard for the Installation of Standpipe and Hose Systems NFPA 15, Standard for Water Spray Fixed Systems for Fire Protection NFPA 16, Standard for the Installation of Foam-Water Sprinkler and Foam-Water Spray Systems NFPA 20, Standard for the Installation of Stationary Fire Pumps for Fire Protection Spray Systems NFPA 750, Standard on Water Mist Fire Protection Systems NMA Regulations No.67, Regulation concerning ballast systems on mobile offshore units (Ballast Regulations) NMA Regulations No. 90, Evacuation and Life-saving appliances on mobile offshore units NMA Regulations No. 123, Regulation for mobile offshore units with production plants and equipment NMA Regulations No. 998, Regulation concerning positioning and anchoring systems on mobile offshore units For the purposes of this NORSOK standard, the following terms, definitions and abbreviations apply. 3.1 shall (requirement) expression in the content of a document conveying objectively verifiable criteria to be fulfilled and from which no deviation is permitted if compliance with the document is to be claimed Note 1 to entry: Requirements are expressed using the verbal forms specified in ISO/IEC Directives, Part 2 clause 7.2 Table 3. 3.2 should (recommendation) expression in the content of a document conveying a suggested possible choice or course of action deemed to be particularly suitable without necessarily mentioning or excluding others NORSOK S-001:2018 NORSOK © 2018 Note 1 to entry: Recommendations are expressed using the verbal forms specified in ISO/IEC Directives, Part 2 clause 7.3 Table 4. Note 2 to entry: In the negative form, a recommendation is the expression that a suggested possible choice or course of action is not preferred but it is not prohibited. 3.3 may (permission) expression in the content of a document conveying consent or liberty (or opportunity) to do something Note 1 to entry: Permissions are expressed using the verbal forms specified in ISO/IEC Directives Part 2 clause 7.Table 5. 3.can (possibility and capability) 1: expression in the content of a document conveying expected or conceivable material, physical or causal outcome. 2: expression in the content of a document conveying the ability, fitness, or quality necessary to do or achieve a specified thing Note 1 to entry: Possibility and capability is expressed using the verbal forms specified in in ISO/IEC Directives, Part 2 clause 7.5 Table 6. 3.5 area classification division of an installation into hazardous areas and non-hazardous areas and the sub-division of hazardous zones under normal operation. Note 1 to entry: Normal operation is a situation when the plant is operating within its design parameters. Minor releases of flammable material may be part of normal operation. For example, releases from seals that rely on wetting by the fluid being pumped are considered to be minor releases. Failures (such as breakdown of pump seals, flange gaskets or spillage caused by accidents) that involve repair or shutdown are not considered to be part of normal operation, and may require special precautions of potential ignition sources. 3.6 design accidental load accidental load/action used as a basis for design Note 1 to entry: The design load/action can be the same as the dimensioning accidental load/action, but it can be higher, based on different input and assessments such as ALARP, minimum requirements in the regulations etc. 3.7 design fire the design fire for load bearing structures and fire divisions includes as a minimum: the dimensioning fire worst credible process fire fire class requirements, e.g. H-class 3.8 detection area area, or areas, of similar environmental and operating conditions and hazards, and with similar detection and protection arrangements. NORSOK S-001:2018 NORSOK © 2018 5 Note 1 to entry: For HC areas, the detection area is normally similar to the fire area in question. Very large fire areas may exceptionally be split into two or more detection areas, e.g. large tank decks on FPSOs. Each detection area will have a C&E Diagram, e.g. FPDS. 3.9 dimensioning accidental load an accidental load/action that a function or a system shall be able to withstand for a given period of time to meet the defined acceptance criteria for risk 3.10 dimensioning gas cloud the minimum stoichiometric gas cloud which, when ignited, can create an explosion resulting in an explosion pressure exceeding the dimensioning explosion load of the area 3.11 escape route route from an area of an installation leading to a muster or embarkation area. 3.12 essential equipment equipment that shall be kept alive to maintain production or drilling/well operations. Note 1 to entry: Such equipment may include main power generator, main electrical distribution panels, diesel engines, heaters, boilers ventilation systems, unless defined as a safety critical item 3.13 evacuation planned method of leaving the installation in an emergency situation 3.1evaluation a simplified assessment which does not require to be documented in a separate analysis or study report Note 1 to entry: The reasoning and conclusions should be described e.g. in the safety strategy. 3.15 explosion load the load generated by combustion of a flammable gas or mist which generates pressure and drag effects 3.16 fire area area separated from other areas either by physical barriers (fire/blast division) or sufficient distance which will prevent a fire or explosion to spread to another fire area when exposed to the design loads. 3.17 fire load time and space dependent radiative and convective heat load from a fire 3.18 fire water (FW) pump system total system which supplies water for firefighting system Note 1 to entry: i.e. water inlets with filters, FW pumps, risers, power sources, power transmissions, fuel pipes/tanks and control systems NORSOK S-001:2018 6 NORSOK © 2018 3.19 hazardous area an area in which a flammable atmosphere is or may be expected to be present in quantities such as to require special precautions for the control of potential ignition sources 3.20 ignition Source equipment and activities which may under certain circumstances cause ignition of an explosive atmosphere Note 1 to entry: Typically ignition sources relate to the following type of equipment; non Ex-certified electrical equipment (or not approved for Zone 2), open flames, direct heat and hot surfaces, rotating machinery and combustion engines, mechanical sparks, static electricity, radio frequency energy, chemical reaction (e.g. iron sulphide). Note 2 to entry: Electrical equipment will not constitute an ignition source if in compliance with relevant IEC zone requirements or better. 3.21 ignition source groups Group 1 (non-essential equipment): non-explosion protected equipment which is not affecting production availability or safety integrity. Group 2 (essential equipment): non-explosion protected equipment which shall be kept alive to maintain production and drilling operation. Group 3 (safety critical equipment): non-explosion protected equipment that shall be in operation to ensure rescue and medical treatment of injured personnel, escape and evacuation, prevent escalation or bring the installation to a safe state. 3.22 inhibit disabling of the safety instrumented function input and prevention of a shutdown action; Note 1 to entry: e.g. by disabling of the input signal to the shutdown logic while still presenting the alarm to the operator 3.23 intermittently manned work area or work place where inspection, maintenance or other work is planned to last at least 2 h, but less than 8 h a day for at least 50 % of the installation™s operation time 3.2local equipment room (LER a room containing electrical and instrumentation equipment 3.25 main area area that includes similar functions on the installation. Note 1 to entry: Main areas can be the: a) living quarter b) utility area c) drilling area d) wellhead area e) process area f) storage area for hydrocarbons Note 2 to entry: Drilling and wellhead area may be combined. See subclause 20.4.1. NORSOK S-001:2018 NORSOK © 2018 7 3.26 muster area designated area where mustering shall take place in the event of general and/or evacuation alarm, and where personnel is sheltered while emergency response and evacuation pre-planning are undertaken 3.27 non-essential equipment any equipment not affecting production availability or safety integrity 3.28 non-hazardous area all areas not classified as hazardous under normal operation 3.29 normally not manned area work area or work place that is not permanently or intermittently manned. 3.30 normally not manned installations installations that can be left unmanned and still maintain their intended function through remote control 3.31 override disabling of the safety instrumented function output and prevention of a shutdown action, e.g. by disabling the signal from shutdown logic to an individual shutdown output action. 3.32 permanently manned work area or work place manned at least 8 hours a day for at least 50 % of the installations operation time 3.33 safety critical equipment equipment that shall be in operation to ensure rescue and medical treatment of injured personnel, escape and evacuation, prevent escalation or bring the installation to a safe state, Note 1 to entry: e.g. equipment powered from UPS and/or emergency generator(s), fire water pump drivers, etc. Ignition source Group 3, see definition, is a sub-group of this equipment. 3.3well barrier envelope of one or several barrier elements preventing well fluids from flowing unintentionally from the formation into another formation or to surface. For this document, the following abbreviations apply. AC/h air changes per hour AFP active fire protection AIS automatic identification system API American Petroleum Institute NORSOK S-001:2018 8 NORSOK © 2018 APS abandon platform shutdown ASV annular safety valve ASME American Society of Mechanical Engineers ATEX Atmosphères Explosibles (forskrift om utstyr og sikkerhetssystem til bruk i eksplosjonsfarlig område) BOP blow out preventer C&E cause and effect CAP critical action panel CCR central control room DHSV down hole safety valve DIFFS deck integrated firefighting system EDP Emergency Depressurisation EER evacuation, escape and rescue EN European Standard ESD emergency shutdown F&G fire and gas FPDS fire protection data sheet FPSO floating production, storage and offloading FSU floating storage unit FW fire water HC hydrocarbon HMI human machine interface HVAC heating, ventilation and air conditioning IEC International Electrotechnical Commission IMO International Maritime Organisation IDLH Immediate Danger to Life and Health ISC ignition source control ISO International Organization for Standardization IR infrared LAHH level alarm high high (trip level) LCS loading computer system LEL lower explosive limit LELm lower explosive limit meters LER local equipment room LIR local instrument room LQ living quarter MCP manual call point MOB man over board NORSOK S-001:2018 NORSOK © 2018 9 MODU mobile offshore drilling unit MV master valve NA not applicable NFPA National Fire Protection Association NMA Norwegian Maritime Authority NNMI normally not manned installations PA public address PAGA public address and general alarm PFD probability of failure on demand PFP passive fire protection PSD process shutdown PSV pressure safety valve RIO Remote input/output SAS safety and automation system SIL safety integrity level SOLAS International Convention for the Safety of Life at Sea SSIV subsea isolation valve UHF ultra high frequency VDU visual display unit UPS uninterruptible power supply VHF very high frequency WV wing valve Technical safety management (loss prevention) in project development comprises activities to identify risks and to develop and document safety strategies and performance requirements for safety systems and barriers. These are iterative processes as the project develops and design matures. Necessary supporting documentation (e.g. studies, analysis and design reviews) shall be provided with due consideration for timely input to design and procurement processes. Concepts combining a jack-up drilling rig and a fixed installation require special consideration, ref. aspects described in Annex A - Jack-up/jacket constellations. A follow-up system shall be established that enables proper documentation, handling, follow-up and closeout of agreed actions and recommendations from the various studies and analyses in the project. In the event space is allocated for future expansions in new project developments, the design should incorporate sufficient flexibility to include capacity for the additional equipment, e.g. fire water, flare etc. fire water. NORSOK S-001:2018 10 NORSOK © 2018 For modification projects (e.g. upgrading of existing installation/module, tie-in of satellite field), technical safety management activities adjusted to project scope and complexity shall be performed, including new analyses or updating of existing analyses for factors that are affected by the modification. The individual project or installation shall perform specific hazard identification and risk analysis and evaluation processes. Based on this process, the requirements in this document shall be supplemented as necessary to manage the risk. 5.2
15 | 5.2 Activities related to technical safety design
16
17
18
19 | 5.2.1 Overview
20 | A flow diagram illustrating some of the main activities related to technical safety design is shown in Figure 1. The activities are detailed in the immediate following subclauses. Reference is made to NORSOK Z-013 for details related to risk assessment. Figure 1 Š
21 | 5.2.2 Define context
22
23
24
25 | 5.2.3 Identify hazards and accidental events (HAZID)
26 | The starting point for the risk assessment is to identify hazards and their accidental events that are relevant for the design and operation of the installation. Within management of technical safety, various hazard identifications need to be performed. The structure of HAZIDs should preferably be area based, but for some cases they may also be a HAZID node (e.g. part of well, process or utility systems), phase or operational based. Based on hazard identifications it shall be possible to present an overview of possible hazards and accidental events that can occur in different areas and during different activities. The level of detail and depth of hazard identification will be dependent of the maturity of the projects.
27 | 5.2.4 Perform risk analyses and evaluations
28
29
30
31 | 5.2.5 Identify and define barrier functions, systems and elements (risk treatment)
32 | The need for barrier functions shall be established based on the context, identified hazards and accidental events, risk analyses and risk evaluation activities. Documentation shall be prepared so that it is possible to identify the need for barrier functions in each installation area or relevant HAZID node. When the need for barrier functions are identified, systems and elements necessary for realizing the barrier functions shall be defined. Technical barriers often require some form of monitoring, control or activation by people to function as intended. Depending on the characteristics of the facility and its risk picture, different levels of automation may also be chosen for certain safety systems. Therefore, operational and emergency situation considerations shall be an integral part of technical barrier process. As part of project development, safety system design shall include a human factors study amongst others documenting the following: Identification of safety critical tasks (ﬁoperational barrier elementsﬂ) required for the safety system to function. These include tasks related to start-up, monitoring, operation, incident response and recovery in the event of technical failure. Description of performance requirements. These include who is responsible for performing a task, under what circumstances it is expected to be performed, available response time and how it shall be carried out. The results from the study shall be used as input to design, as well as preparations for operations. Input to design should include HMI and alarm system specifications, levels of automation, equipment labelling, system capacities and tolerances. This standard focuses on technical design requirements and addresses operational and organizational aspects supplementing the technical barriers.
33 | 5.2.6 Safety strategies
34
35
36
37 | 5.2.7 Define performance requirements
38 | Verifiable performance requirements shall be established to ensure that the barrier function is fulfilled. In some situations, performance requirements can also be set directly to barrier functions. Performance requirements shall be established as an integrated part of the design and construction process, as the decisions on what safety systems and barriers to install and their corresponding specifications are made. Performance requirement (PR) for technical barrier elements can be divided into the following categories: Functionality i.e. the ability of the barrier or barrier element to execute the objectives (intended role) affecting the progress of an accident, e.g. by ensuring capacity and effectiveness. The NORSOK S-001:2018 NORSOK © 2018 13 minimum functional requirement of barrier/barrier element is often given by regulations, referred standards and company internal requirements. However, the specific safety strategy can call for stricter or more nuanced requirements. Integrity of the barrier/barrier element, i.e. the barrier / barrier element™s ability to be present when needed (reliability and availability). These requirements can be determined based on specific safety analysis-/studies or the implementation of generic minimum requirements. The following general requirements apply: o Design and realisation, inclusive of relevant operating issues, of all safety instrumented systems (SIS) shall be based upon the principles of IEC 61508/IEC 61511. The minimum requirements presented in Norwegian Oil and Gas Association GL070 may be used instead of a full safety analysis/risk assessment for standardised solutions. o The applicable safety system, or affected parts of it, shall be designed to fail-to-safe principle, whereby the system goes to a predefined safe state in the event of detectable malfunction. It shall be designed with the aim of avoiding single defects / failures that may prohibit safety actions being executed. If it is not feasible to implement a fail-to-safe principle, an equivalent level of safety shall be achieved by redundancy and/or diagnostics and fault alarm to relevant manned control room. o The probability of single defects / failures causing inadvertent trip actions shall be as low as reasonably practicable (e.g. provide fault tolerance by means of automatic diagnostic features and redundancy). o All barriers or parts thereof, shall be protected against or withstand environmental conditions that may compromise their safety functions, e.g. ice, snow, sand, water, etc. Survivability of the barrier/barrier element, i.e. its ability to function under relevant accident scenarios and loads. Equipment with a safety function, during and after the accident, should be located so that the possible impact from accidental loads is minimised. To develop the survivability requirements, the design loads that shall form the basis for design of facilities, systems and equipment need to be determined, ref. subclause 5.6 Accidental loads and resistance. Barriers/safety systems may be dependent on safety critical tasks to function, through e.g. monitoring, activation or control. For relevant safety systems, performance requirements should also be defined for operational / organizational barrier elements, ref. subclause 5.4. Each clause of this document from clause 6 and onwards describes generic design principles and requirements for the different safety systems and barriers. The installation specific performance requirements shall be developed based on this framework to manage the risk.
39 | 5.2.8 Define performance Standards
40
41
42
43 | 5.2.9 Establish safety requirement specification (SRS)
44 | A Safety Requirement Specification (SRS) is a documentation of requirements related to safety instrumented systems (SIS). The SRS documentation shall be developed during projects and shall provide the design basis for required SIS.ly, the SRS shall contain the relevant key information for use in specifying and operating the instrumented safety functions. However, the information required may be contained in other project documents referred to in the SRS, e.g. performance standards. Duplication of information should be avoided. The SRS shall contain three main types of requirements: NORSOK S-001:2018 1NORSOK © 2018 functional requirements such as capacities and response times, integrity requirements such as PFD and SIL, and, operating prerequisites and constraints. Further reference is given to IEC 61511 (Functional Safety Œ Safety Instrumented Systems for the process industry sectorﬂ) and Norwegian Oil and Gas Association GL070.
45 | 5.2.10 Safety specifications, diagrams, drawings, philosophies, etc.
46
47
48
49 | 5.3 Risk reduction principles and inherent safety design
50
51
52
53 | 5.4 Design provisions for the operating phase
54
55
56
57 | 5.5 Commissioning and start-up
58 | 5.6 Accidental loads and resistance
59
60
61
62 | 5.6.1 General
63
64
65
66 | 5.6.2 Gas explosions
67 | Explosion loads from ignited gas clouds are strongly dependent on factors such as: cloud size and gas concentration; gas type; confinement and/or congestion of the affected area; explosion relief solutions; ignition location. Design explosion loads shall be established using a recognised method (e.g. NORSOK Z-013) and a representative geometric explosion model with representative equipment density. It is recognized that in the initial design the detail arrangement may not have been developed. An explosion study should be performed at an early stage, enabling the key installation parts to be located favorably with regard to explosion. The methods and detailing of the input will reflect this situation. Explosion loads shall be defined for relevant horizontal and vertical area dividers (pressure and impulse from explosion) and relevant equipment (pressure/drag forces). Explosion loads shall also be defined for areas external to the initial explosion location (typical LQ, utility modules etc.) if applicable. Equipment that can become a flying object and can significantly impair critical safety equipment/structures such as fire divisions, riser valves, wellheads, blowdown piping, should be considered secured. Examples of such equipment are well hatches, panels, temporary equipment, etc.
68 | 5.6.3 Hydrocarbon fires
69
70
71
72 | 5.6.3.1 General
73
74
75
76 | 5.6.3.2 Main load bearing structures
77 | 5.6.3.3 Worst credible process fire
78
79 | NORSOK © 2018 1 NORSOK Standard NORSOK S-001:2018 Technical Safety This NORSOK standard describes the principles and requirements for the development of the physical safety design, i.e. technical safety, of offshore installations for production of oil and gas. Where applicable, this NORSOK standard may also be used for mobile offshore drilling units. This NORSOK standard, together with ISO 13702, defines the required standard to establish and maintain an adequate level of safety for personnel, environment and material assets. The following standards include provisions and guidelines which, through reference in this text, constitute provisions and guidelines of this NORSOK standard. Latest issue of the references shall be used unless otherwise agreed. Other recognized standards may be used provided it can be shown that they meet the requirements of the referenced standards. NORSOK C-001, Living quarters area NORSOK C-002:2015, Architectural components and equipment NORSOK C-004:2013, Helicopter Deck on Offshore Installations NORSOK D-001, Drilling facilities NORSOK D-010, Well integrity in drilling and well operations NORSOK H-003, Heating, ventilation and air conditioning (HVAC) and sanitary systems NORSOK L-001, Piping and valves NORSOK L-002, Piping design, layout and stress analysis NORSOK L-005, Compact flanged connections NORSOK N-001, Structural design NORSOK N-003, Actions and action effects NORSOK N-005, In-service integrity management of structures and maritime systems NORSOK P-002, Process System Design NORSOK R-002, Lifting Equipment NORSOK T-001, Telecom Systems NORSOK T-100, Telecom Subsystems NORSOK Z-008, Risk based maintenance and consequence classification NORSOK Z-013, Risk and emergency preparedness analysis NORSOK Z-015, Temporary Equipment NORSOK S-001:2018 2 NORSOK © 2018 CENELEC CLC/TR 50427, Assessment of inadvertent ignition of flammable atmospheres by radio-frequency radiation EN 5all parts, Fire Detection and Alarm Systems EN 403, Respiratory protective devices for self-rescue - Filtering devices with hood for escape from fire - Requirements, testing, marking EN 1127-1, Explosive atmospheres - Explosion prevention and protection - Part 1: Basic concepts and methodology EN 1838, Lighting applications Œ Emergency lighting EN 12266-1, Industrial valves - Testing of metallic valves - Part 1: Pressure tests, test procedures and acceptance criteria - Mandatory requirements EN 12266-2, Industrial valves - Testing of metallic valves - Part 2: Tests, test procedures and acceptance criteria - Supplementary requirements EN 62682 Management of alarms systems for the process industries ISO 10418:2003/AC:2009, Petroleum and natural gas industries Œ Offshore production installations Œ Basic surface process safety systems ISO 10423, Petroleum and natural gas industries - Drilling and production equipment - Wellhead and christmas tree equipment ISO 10497, Testing of valves - Fire type-testing requirements ISO 13702:2015, Petroleum and natural gas industries Œ Control and mitigation of fires and explosions on offshore production installations Œ Requirements and guidelines ISO 15138, Petroleum and natural gas industries - Offshore production installations - Heating, ventilation and air-conditioning ISO 16069, Graphical Symbols Œ Safety Signs -- Safety Way Guidance System (SWGS) ISO 22899, Determination of the resistance to jet fires of passive fire protection materials -- Part 1: requirements ISO 80079-36. Explosive atmospheres - Part 36: Non-electrical equipment for explosive atmospheres - Basic method and requirements IEC 60079(part 10, part 14:2013/COR1:2016 and part 29), Explosive atmospheres IEC 60331(all parts), Tests for electric cables under fire conditions Œ Circuit integrity IEC 61508(all parts), Functional safety of electrical/electronic/programmable electronic safety-related systems IEC 61511(all parts), Functional safety Œ Safety instrumented systems for the process industry sector IEC 61892(parts 1, 2, 3, 5, 6:2013 and 7) Mobile and fixed offshore units Œ Electrical installations API RP 14C:2017, Recommended Practice for Analysis, Design, Installation, and Testing of Basic Surface Safety Systems for Offshore Production Platforms (8th ed) API Spec 17J, Specification for Unbonded Flexible Pipe API STD 520, Sizing, Selection, and Installation of Pressure-relieving Devices API STD 521, Pressure-Relieving and Depressurizing Systems Directive 94/9/EC, Concerning equipment and protective systems intended for use in potentially explosive atmospheres (ATEX ﬁProductﬂ) DNVGL-ST-E406, Design of Free Fall Lifeboats DNVGL-ST-F201, Dynamic risers NORSOK S-001:2018 NORSOK © 2018 3 EEMUA 191 Alarm systems - a guide to design, management and procurement EI 15, Model code of safe practice Part 15: Area classification code for installations handling flammable fluids LSA Code, IMO SOLAS Life saving appliances (LSA) Code, adopted by the Maritime Safety Committee by resolution MSC.48 (66) Norwegian Oil and Gas Association GL064, Anbefalte retningslinjer for etablering av områdeberedskap Norwegian Oil and Gas Association GL070, Guidelines for the Application of IEC 61508 and IEC 61511 in the petroleum activities on the continental shelf Norwegian Oil and Gas Association GL075, Anbefalte retningslinjer for vannbaserte brannbekjempelsessystemer Norwegian Oil and Gas Association GL094, Kravspesifikasjoner for redningsdrakt til bruk på norsk kontinentalsokkel. MODU Code, Code for the construction and equipment of mobile offshore drilling units NFPA 11, Standard for Low-, Medium-, and High-Expansion Foam NFPA 13, Installation of Sprinkler Systems NFPA 14, Standard for the Installation of Standpipe and Hose Systems NFPA 15, Standard for Water Spray Fixed Systems for Fire Protection NFPA 16, Standard for the Installation of Foam-Water Sprinkler and Foam-Water Spray Systems NFPA 20, Standard for the Installation of Stationary Fire Pumps for Fire Protection Spray Systems NFPA 750, Standard on Water Mist Fire Protection Systems NMA Regulations No.67, Regulation concerning ballast systems on mobile offshore units (Ballast Regulations) NMA Regulations No. 90, Evacuation and Life-saving appliances on mobile offshore units NMA Regulations No. 123, Regulation for mobile offshore units with production plants and equipment NMA Regulations No. 998, Regulation concerning positioning and anchoring systems on mobile offshore units For the purposes of this NORSOK standard, the following terms, definitions and abbreviations apply. 3.1 shall (requirement) expression in the content of a document conveying objectively verifiable criteria to be fulfilled and from which no deviation is permitted if compliance with the document is to be claimed Note 1 to entry: Requirements are expressed using the verbal forms specified in ISO/IEC Directives, Part 2 clause 7.2 Table 3. 3.2 should (recommendation) expression in the content of a document conveying a suggested possible choice or course of action deemed to be particularly suitable without necessarily mentioning or excluding others NORSOK S-001:2018 NORSOK © 2018 Note 1 to entry: Recommendations are expressed using the verbal forms specified in ISO/IEC Directives, Part 2 clause 7.3 Table 4. Note 2 to entry: In the negative form, a recommendation is the expression that a suggested possible choice or course of action is not preferred but it is not prohibited. 3.3 may (permission) expression in the content of a document conveying consent or liberty (or opportunity) to do something Note 1 to entry: Permissions are expressed using the verbal forms specified in ISO/IEC Directives Part 2 clause 7.Table 5. 3.can (possibility and capability) 1: expression in the content of a document conveying expected or conceivable material, physical or causal outcome. 2: expression in the content of a document conveying the ability, fitness, or quality necessary to do or achieve a specified thing Note 1 to entry: Possibility and capability is expressed using the verbal forms specified in in ISO/IEC Directives, Part 2 clause 7.5 Table 6. 3.5 area classification division of an installation into hazardous areas and non-hazardous areas and the sub-division of hazardous zones under normal operation. Note 1 to entry: Normal operation is a situation when the plant is operating within its design parameters. Minor releases of flammable material may be part of normal operation. For example, releases from seals that rely on wetting by the fluid being pumped are considered to be minor releases. Failures (such as breakdown of pump seals, flange gaskets or spillage caused by accidents) that involve repair or shutdown are not considered to be part of normal operation, and may require special precautions of potential ignition sources. 3.6 design accidental load accidental load/action used as a basis for design Note 1 to entry: The design load/action can be the same as the dimensioning accidental load/action, but it can be higher, based on different input and assessments such as ALARP, minimum requirements in the regulations etc. 3.7 design fire the design fire for load bearing structures and fire divisions includes as a minimum: the dimensioning fire worst credible process fire fire class requirements, e.g. H-class 3.8 detection area area, or areas, of similar environmental and operating conditions and hazards, and with similar detection and protection arrangements. NORSOK S-001:2018 NORSOK © 2018 5 Note 1 to entry: For HC areas, the detection area is normally similar to the fire area in question. Very large fire areas may exceptionally be split into two or more detection areas, e.g. large tank decks on FPSOs. Each detection area will have a C&E Diagram, e.g. FPDS. 3.9 dimensioning accidental load an accidental load/action that a function or a system shall be able to withstand for a given period of time to meet the defined acceptance criteria for risk 3.10 dimensioning gas cloud the minimum stoichiometric gas cloud which, when ignited, can create an explosion resulting in an explosion pressure exceeding the dimensioning explosion load of the area 3.11 escape route route from an area of an installation leading to a muster or embarkation area. 3.12 essential equipment equipment that shall be kept alive to maintain production or drilling/well operations. Note 1 to entry: Such equipment may include main power generator, main electrical distribution panels, diesel engines, heaters, boilers ventilation systems, unless defined as a safety critical item 3.13 evacuation planned method of leaving the installation in an emergency situation 3.1evaluation a simplified assessment which does not require to be documented in a separate analysis or study report Note 1 to entry: The reasoning and conclusions should be described e.g. in the safety strategy. 3.15 explosion load the load generated by combustion of a flammable gas or mist which generates pressure and drag effects 3.16 fire area area separated from other areas either by physical barriers (fire/blast division) or sufficient distance which will prevent a fire or explosion to spread to another fire area when exposed to the design loads. 3.17 fire load time and space dependent radiative and convective heat load from a fire 3.18 fire water (FW) pump system total system which supplies water for firefighting system Note 1 to entry: i.e. water inlets with filters, FW pumps, risers, power sources, power transmissions, fuel pipes/tanks and control systems NORSOK S-001:2018 6 NORSOK © 2018 3.19 hazardous area an area in which a flammable atmosphere is or may be expected to be present in quantities such as to require special precautions for the control of potential ignition sources 3.20 ignition Source equipment and activities which may under certain circumstances cause ignition of an explosive atmosphere Note 1 to entry: Typically ignition sources relate to the following type of equipment; non Ex-certified electrical equipment (or not approved for Zone 2), open flames, direct heat and hot surfaces, rotating machinery and combustion engines, mechanical sparks, static electricity, radio frequency energy, chemical reaction (e.g. iron sulphide). Note 2 to entry: Electrical equipment will not constitute an ignition source if in compliance with relevant IEC zone requirements or better. 3.21 ignition source groups Group 1 (non-essential equipment): non-explosion protected equipment which is not affecting production availability or safety integrity. Group 2 (essential equipment): non-explosion protected equipment which shall be kept alive to maintain production and drilling operation. Group 3 (safety critical equipment): non-explosion protected equipment that shall be in operation to ensure rescue and medical treatment of injured personnel, escape and evacuation, prevent escalation or bring the installation to a safe state. 3.22 inhibit disabling of the safety instrumented function input and prevention of a shutdown action; Note 1 to entry: e.g. by disabling of the input signal to the shutdown logic while still presenting the alarm to the operator 3.23 intermittently manned work area or work place where inspection, maintenance or other work is planned to last at least 2 h, but less than 8 h a day for at least 50 % of the installation™s operation time 3.2local equipment room (LER a room containing electrical and instrumentation equipment 3.25 main area area that includes similar functions on the installation. Note 1 to entry: Main areas can be the: a) living quarter b) utility area c) drilling area d) wellhead area e) process area f) storage area for hydrocarbons Note 2 to entry: Drilling and wellhead area may be combined. See subclause 20.4.1. NORSOK S-001:2018 NORSOK © 2018 7 3.26 muster area designated area where mustering shall take place in the event of general and/or evacuation alarm, and where personnel is sheltered while emergency response and evacuation pre-planning are undertaken 3.27 non-essential equipment any equipment not affecting production availability or safety integrity 3.28 non-hazardous area all areas not classified as hazardous under normal operation 3.29 normally not manned area work area or work place that is not permanently or intermittently manned. 3.30 normally not manned installations installations that can be left unmanned and still maintain their intended function through remote control 3.31 override disabling of the safety instrumented function output and prevention of a shutdown action, e.g. by disabling the signal from shutdown logic to an individual shutdown output action. 3.32 permanently manned work area or work place manned at least 8 hours a day for at least 50 % of the installations operation time 3.33 safety critical equipment equipment that shall be in operation to ensure rescue and medical treatment of injured personnel, escape and evacuation, prevent escalation or bring the installation to a safe state, Note 1 to entry: e.g. equipment powered from UPS and/or emergency generator(s), fire water pump drivers, etc. Ignition source Group 3, see definition, is a sub-group of this equipment. 3.3well barrier envelope of one or several barrier elements preventing well fluids from flowing unintentionally from the formation into another formation or to surface. For this document, the following abbreviations apply. AC/h air changes per hour AFP active fire protection AIS automatic identification system API American Petroleum Institute NORSOK S-001:2018 8 NORSOK © 2018 APS abandon platform shutdown ASV annular safety valve ASME American Society of Mechanical Engineers ATEX Atmosphères Explosibles (forskrift om utstyr og sikkerhetssystem til bruk i eksplosjonsfarlig område) BOP blow out preventer C&E cause and effect CAP critical action panel CCR central control room DHSV down hole safety valve DIFFS deck integrated firefighting system EDP Emergency Depressurisation EER evacuation, escape and rescue EN European Standard ESD emergency shutdown F&G fire and gas FPDS fire protection data sheet FPSO floating production, storage and offloading FSU floating storage unit FW fire water HC hydrocarbon HMI human machine interface HVAC heating, ventilation and air conditioning IEC International Electrotechnical Commission IMO International Maritime Organisation IDLH Immediate Danger to Life and Health ISC ignition source control ISO International Organization for Standardization IR infrared LAHH level alarm high high (trip level) LCS loading computer system LEL lower explosive limit LELm lower explosive limit meters LER local equipment room LIR local instrument room LQ living quarter MCP manual call point MOB man over board NORSOK S-001:2018 NORSOK © 2018 9 MODU mobile offshore drilling unit MV master valve NA not applicable NFPA National Fire Protection Association NMA Norwegian Maritime Authority NNMI normally not manned installations PA public address PAGA public address and general alarm PFD probability of failure on demand PFP passive fire protection PSD process shutdown PSV pressure safety valve RIO Remote input/output SAS safety and automation system SIL safety integrity level SOLAS International Convention for the Safety of Life at Sea SSIV subsea isolation valve UHF ultra high frequency VDU visual display unit UPS uninterruptible power supply VHF very high frequency WV wing valve Technical safety management (loss prevention) in project development comprises activities to identify risks and to develop and document safety strategies and performance requirements for safety systems and barriers. These are iterative processes as the project develops and design matures. Necessary supporting documentation (e.g. studies, analysis and design reviews) shall be provided with due consideration for timely input to design and procurement processes. Concepts combining a jack-up drilling rig and a fixed installation require special consideration, ref. aspects described in Annex A - Jack-up/jacket constellations. A follow-up system shall be established that enables proper documentation, handling, follow-up and closeout of agreed actions and recommendations from the various studies and analyses in the project. In the event space is allocated for future expansions in new project developments, the design should incorporate sufficient flexibility to include capacity for the additional equipment, e.g. fire water, flare etc. fire water. NORSOK S-001:2018 10 NORSOK © 2018 For modification projects (e.g. upgrading of existing installation/module, tie-in of satellite field), technical safety management activities adjusted to project scope and complexity shall be performed, including new analyses or updating of existing analyses for factors that are affected by the modification. The individual project or installation shall perform specific hazard identification and risk analysis and evaluation processes. Based on this process, the requirements in this document shall be supplemented as necessary to manage the risk. 5.2 A flow diagram illustrating some of the main activities related to technical safety design is shown in Figure 1. The activities are detailed in the immediate following subclauses. Reference is made to NORSOK Z-013 for details related to risk assessment. Figure 1 Š Context needs to be defined and compiled so that frame conditions, limitations and ambitions for the installation (and its areas and activities) are available for relevant personnel involved in technical safety issues or technical safety management. Examples of context are legislation, standards (internal/ external), concept decisions, operating conditions, prerequisites for use, assumptions/ requirements and NORSOK S-001:2018 NORSOK © 2018 11 demands to risk reduction. The context applied for the management of technical safety has to be traceable and documented. A major part of the context will be defined early in the development of an installation. During the installation life cycle the context will provide a basis for use/ reassessment and it need to be updated to ensure that all relevant changes and modifications are included. The starting point for the risk assessment is to identify hazards and their accidental events that are relevant for the design and operation of the installation. Within management of technical safety, various hazard identifications need to be performed. The structure of HAZIDs should preferably be area based, but for some cases they may also be a HAZID node (e.g. part of well, process or utility systems), phase or operational based. Based on hazard identifications it shall be possible to present an overview of possible hazards and accidental events that can occur in different areas and during different activities. The level of detail and depth of hazard identification will be dependent of the maturity of the projects. Risk and safety analyses / studies shall be performed to establish sufficiently detailed information about the risk associated with the identified hazards and accidental events. The information will be used to evaluate the risk and to decide which solutions (barriers), and related requirements that are needed for preventing, controlling and mitigating the hazards in addition to generic requirements given by the context. Evaluation of risk includes an assessment of: compliance with predefined evaluation criteria (e.g. minimum requirements and acceptance criteria in context); necessary ALARP processes to demonstrate that risk has been reduced to a level as low as reasonably practicable; uncertainties associated with the hazards, accidental events and their consequences as well as the risk reducing effect of the barriers. The results from risk analyses are used for many purposes. One is to provide information and decision support related to the need for and role of risk reducing measures (barriers) and their required performance. Another is to provide decision support regarding the risk level assessed and if this is considered acceptable for the facility. Reference is made to subclause 5.10 for examples of studies and evaluations. For a development project, the degree of details in the risk and safety analyses / studies will increase as the project matures through different phases. Thus, solutions, assumptions and conservative estimates typically used in early stages may be verified or changed due to more detailed analyses. The need for barrier functions shall be established based on the context, identified hazards and accidental events, risk analyses and risk evaluation activities. Documentation shall be prepared so that it is possible to identify the need for barrier functions in each installation area or relevant HAZID node. When the need for barrier functions are identified, systems and elements necessary for realizing the barrier functions shall be defined. Technical barriers often require some form of monitoring, control or activation by people to function as intended. Depending on the characteristics of the facility and its risk picture, different levels of automation may also be chosen for certain safety systems. Therefore, operational and emergency situation considerations shall be an integral part of technical barrier process. As part of project development, safety system design shall include a human factors study amongst others documenting the following: Identification of safety critical tasks (ﬁoperational barrier elementsﬂ) required for the safety system to function. These include tasks related to start-up, monitoring, operation, incident response and recovery in the event of technical failure. Description of performance requirements. These include who is responsible for performing a task, under what circumstances it is expected to be performed, available response time and how it shall be carried out. The results from the study shall be used as input to design, as well as preparations for operations. Input to design should include HMI and alarm system specifications, levels of automation, equipment labelling, system capacities and tolerances. This standard focuses on technical design requirements and addresses operational and organizational aspects supplementing the technical barriers. Documentation shall be prepared to record how specific hazards or accidental events are managed by the use of barrier functions, systems and elements. This documentation can be denoted the 'safety strategy™ (or ‚the barrier strategy™) and can replace the need for Fire and Explosion Strategy (FES) and the Escape, Evacuation and Rescue Strategy (EER strategy) as required by ISO 13702. do not necessarily need to be described in a single document. The strategy may be described and included in other relevant documentation where this is natural and appropriate. The need to develop separate strategies can be viewed in relation to the other documentation which exists or is prepared for the individual facility. Safety strategy documentation should also be prepared to outline applicable overall principles for design, layout, arrangement, philosophies and other high-level design and operational aspects related to barriers; e.g.: how different safety documentation are linked together; risk reduction principles - inherent safety design; premises for design; design provisions for the operating phase; accidental loads and resistance. Verifiable performance requirements shall be established to ensure that the barrier function is fulfilled. In some situations, performance requirements can also be set directly to barrier functions. Performance requirements shall be established as an integrated part of the design and construction process, as the decisions on what safety systems and barriers to install and their corresponding specifications are made. Performance requirement (PR) for technical barrier elements can be divided into the following categories: Functionality i.e. the ability of the barrier or barrier element to execute the objectives (intended role) affecting the progress of an accident, e.g. by ensuring capacity and effectiveness. The NORSOK S-001:2018 NORSOK © 2018 13 minimum functional requirement of barrier/barrier element is often given by regulations, referred standards and company internal requirements. However, the specific safety strategy can call for stricter or more nuanced requirements. Integrity of the barrier/barrier element, i.e. the barrier / barrier element™s ability to be present when needed (reliability and availability). These requirements can be determined based on specific safety analysis-/studies or the implementation of generic minimum requirements. The following general requirements apply: o Design and realisation, inclusive of relevant operating issues, of all safety instrumented systems (SIS) shall be based upon the principles of IEC 61508/IEC 61511. The minimum requirements presented in Norwegian Oil and Gas Association GL070 may be used instead of a full safety analysis/risk assessment for standardised solutions. o The applicable safety system, or affected parts of it, shall be designed to fail-to-safe principle, whereby the system goes to a predefined safe state in the event of detectable malfunction. It shall be designed with the aim of avoiding single defects / failures that may prohibit safety actions being executed. If it is not feasible to implement a fail-to-safe principle, an equivalent level of safety shall be achieved by redundancy and/or diagnostics and fault alarm to relevant manned control room. o The probability of single defects / failures causing inadvertent trip actions shall be as low as reasonably practicable (e.g. provide fault tolerance by means of automatic diagnostic features and redundancy). o All barriers or parts thereof, shall be protected against or withstand environmental conditions that may compromise their safety functions, e.g. ice, snow, sand, water, etc. Survivability of the barrier/barrier element, i.e. its ability to function under relevant accident scenarios and loads. Equipment with a safety function, during and after the accident, should be located so that the possible impact from accidental loads is minimised. To develop the survivability requirements, the design loads that shall form the basis for design of facilities, systems and equipment need to be determined, ref. subclause . Barriers/safety systems may be dependent on safety critical tasks to function, through e.g. monitoring, activation or control. For relevant safety systems, performance requirements should also be defined for operational / organizational barrier elements, ref. subclause 5.4. Each clause of this document from clause 6 and onwards describes generic design principles and requirements for the different safety systems and barriers. The installation specific performance requirements shall be developed based on this framework to manage the risk. It may be beneficial to group the various performance requirements into performance standards including a description of the role of the safety functions. Dependencies on and interfaces with other systems should also be described. A Safety Requirement Specification (SRS) is a documentation of requirements related to safety instrumented systems (SIS). The SRS documentation shall be developed during projects and shall provide the design basis for required SIS.ly, the SRS shall contain the relevant key information for use in specifying and operating the instrumented safety functions. However, the information required may be contained in other project documents referred to in the SRS, e.g. performance standards. Duplication of information should be avoided. The SRS shall contain three main types of requirements: NORSOK S-001:2018 1NORSOK © 2018 functional requirements such as capacities and response times, integrity requirements such as PFD and SIL, and, operating prerequisites and constraints. Further reference is given to IEC 61511 (Functional Safety Œ Safety Instrumented Systems for the process industry sectorﬂ) and Norwegian Oil and Gas Association GL070.. Documentation that needs to be developed to deepen or clarify performance requirements when necessary. Ref. subclause 5.10 Documentation. Also, see Annex C for proposed format and information for data sheets for selected Safety Equipment. 5.3 Risk reduction principles and inherent safety design In concept development, priority shall be given to solutions that are inherently safe. If the hazard cannot be eliminated, probability reducing measures should be given priority over consequence reducing measures. The objectives of risk reduction principles and inherent safety design are to: eliminate or reduce potential hazards/increase inherent safety by; reduction, e.g. reducing the hazardous inventories or the frequency or duration of exposure; substitution, e.g. substituting hazardous materials with less hazardous ones; attenuation (moderation), e.g. using the hazardous materials or processes in a way that limits their hazard potential; simplifications, e.g. making the facility and process simpler to design, build and operate, hence less prone to equipment, control and human failure; reduce probability of hazardous events; establish mitigating measures, e.g. through safety barriers. The ALARP principle (As Low As Reasonable Practicable) shall be used to select the safety solutions. 5.Design provisions for the operating phase Effective management of technical barriers in project development and design processes also need to address relevant dependencies with operational and organizational aspects for the operating phase. Some examples of interfaces between technical, operational and organizational aspects to be considered are: operational prerequisites for start-up and use; measures and restrictions that are necessary in the event of overriding, disconnection or in the event of missing/impaired safety systems and barriers; maintenance; competence; emergency preparedness; manual intervention. In order to ensure solutions which are suited for varying conditions, particular prerequisites shall be accommodated for in the design phase (and sustained during the operating phase). Examples of aspects that should be addressed are: assumptions including conditions and possible actions, when operating in different modes, i.e. normal, test, fault, failure, degraded. (Relevant assumptions in risk analyses should be according to requirements in the different installation specific performance standards); NORSOK S-001:2018 NORSOK © 2018 15 provisions, routines and logs for isolation of safety related functions during testing and maintenance, e.g. by inhibit (disabling input signal) and override (disabling output action). Such isolation should not render unnecessarily large parts of the system inactive. Logging, manual o
80 | 5.6.3.4 Unacceptable ruptures of process equipment in a fire situation.
81
82
83
84 | 5.6.3.5 Process equipment and piping – fire calculations
85
86
87
88 | 5.7 Qualification of technology
89 | 5.8 Experience transfer
90
91
92
93 | 5.9 Temporary equipment
94 | 5.10 Documentation
95 | shall be prepared so that it is possible to identify the need for barrier functions in each installation area or relevant HAZID node. When the need for barrier functions are identified, systems and elements necessary for realizing the barrier functions shall be defined. Technical barriers often require some form of monitoring, control or activation by people to function as intended. Depending on the characteristics of the facility and its risk picture, different levels of automation may also be chosen for certain safety systems. Therefore, operational and emergency situation considerations shall be an integral part of technical barrier process. As part of project development, safety system design shall include a human factors study amongst others documenting the following: Identification of safety critical tasks (ﬁoperational barrier elementsﬂ) required for the safety system to function. These include tasks related to start-up, monitoring, operation, incident response and recovery in the event of technical failure. Description of performance requirements. These include who is responsible for performing a task, under what circumstances it is expected to be performed, available response time and how it shall be carried out. The results from the study shall be used as input to design, as well as preparations for operations. Input to design should include HMI and alarm system specifications, levels of automation, equipment labelling, system capacities and tolerances. This standard focuses on technical design requirements and addresses operational and organizational aspects supplementing the technical barriers. Documentation shall be prepared to record how specific hazards or accidental events are managed by the use of barrier functions, systems and elements. This documentation can be denoted the 'safety strategy™ (or ‚the barrier strategy™) and can replace the need for Fire and Explosion Strategy (FES) and the Escape, Evacuation and Rescue Strategy (EER strategy) as required by ISO 13702. do not necessarily need to be described in a single document. The strategy may be described and included in other relevant documentation where this is natural and appropriate. The need to develop separate strategies can be viewed in relation to the other documentation which exists or is prepared for the individual facility. Safety strategy documentation should also be prepared to outline applicable overall principles for design, layout, arrangement, philosophies and other high-level design and operational aspects related to barriers; e.g.: how different safety documentation are linked together; risk reduction principles - inherent safety design; premises for design; design provisions for the operating phase; accidental loads and resistance. Verifiable performance requirements shall be established to ensure that the barrier function is fulfilled. In some situations, performance requirements can also be set directly to barrier functions. Performance requirements shall be established as an integrated part of the design and construction process, as the decisions on what safety systems and barriers to install and their corresponding specifications are made. Performance requirement (PR) for technical barrier elements can be divided into the following categories: Functionality i.e. the ability of the barrier or barrier element to execute the objectives (intended role) affecting the progress of an accident, e.g. by ensuring capacity and effectiveness. The NORSOK S-001:2018 NORSOK © 2018 13 minimum functional requirement of barrier/barrier element is often given by regulations, referred standards and company internal requirements. However, the specific safety strategy can call for stricter or more nuanced requirements. Integrity of the barrier/barrier element, i.e. the barrier / barrier element™s ability to be present when needed (reliability and availability). These requirements can be determined based on specific safety analysis-/studies or the implementation of generic minimum requirements. The following general requirements apply: o Design and realisation, inclusive of relevant operating issues, of all safety instrumented systems (SIS) shall be based upon the principles of IEC 61508/IEC 61511. The minimum requirements presented in Norwegian Oil and Gas Association GL070 may be used instead of a full safety analysis/risk assessment for standardised solutions. o The applicable safety system, or affected parts of it, shall be designed to fail-to-safe principle, whereby the system goes to a predefined safe state in the event of detectable malfunction. It shall be designed with the aim of avoiding single defects / failures that may prohibit safety actions being executed. If it is not feasible to implement a fail-to-safe principle, an equivalent level of safety shall be achieved by redundancy and/or diagnostics and fault alarm to relevant manned control room. o The probability of single defects / failures causing inadvertent trip actions shall be as low as reasonably practicable (e.g. provide fault tolerance by means of automatic diagnostic features and redundancy). o All barriers or parts thereof, shall be protected against or withstand environmental conditions that may compromise their safety functions, e.g. ice, snow, sand, water, etc. Survivability of the barrier/barrier element, i.e. its ability to function under relevant accident scenarios and loads. Equipment with a safety function, during and after the accident, should be located so that the possible impact from accidental loads is minimised. To develop the survivability requirements, the design loads that shall form the basis for design of facilities, systems and equipment need to be determined, ref. subclause . Barriers/safety systems may be dependent on safety critical tasks to function, through e.g. monitoring, activation or control. For relevant safety systems, performance requirements should also be defined for operational / organizational barrier elements, ref. subclause 5.4. Each clause of this document from clause 6 and onwards describes generic design principles and requirements for the different safety systems and barriers. The installation specific performance requirements shall be developed based on this framework to manage the risk. It may be beneficial to group the various performance requirements into performance standards including a description of the role of the safety functions. Dependencies on and interfaces with other systems should also be described. A Safety Requirement Specification (SRS) is a documentation of requirements related to safety instrumented systems (SIS). The SRS documentation shall be developed during projects and shall provide the design basis for required SIS.ly, the SRS shall contain the relevant key information for use in specifying and operating the instrumented safety functions. However, the information required may be contained in other project documents referred to in the SRS, e.g. performance standards. Duplication of information should be avoided. The SRS shall contain three main types of requirements: NORSOK S-001:2018 1NORSOK © 2018 functional requirements such as capacities and response times, integrity requirements such as PFD and SIL, and, operating prerequisites and constraints. Further reference is given to IEC 61511 (Functional Safety Œ Safety Instrumented Systems for the process industry sectorﬂ) and Norwegian Oil and Gas Association GL070.. Documentation that needs to be developed to deepen or clarify performance requirements when necessary. Ref. subclause . Also, see Annex C for proposed format and information for data sheets for selected Safety Equipment. 5.3 Risk reduction principles and inherent safety design In concept development, priority shall be given to solutions that are inherently safe. If the hazard cannot be eliminated, probability reducing measures should be given priority over consequence reducing measures. The objectives of risk reduction principles and inherent safety design are to: eliminate or reduce potential hazards/increase inherent safety by; reduction, e.g. reducing the hazardous inventories or the frequency or duration of exposure; substitution, e.g. substituting hazardous materials with less hazardous ones; attenuation (moderation), e.g. using the hazardous materials or processes in a way that limits their hazard potential; simplifications, e.g. making the facility and process simpler to design, build and operate, hence less prone to equipment, control and human failure; reduce probability of hazardous events; establish mitigating measures, e.g. through safety barriers. The ALARP principle (As Low As Reasonable Practicable) shall be used to select the safety solutions. 5.Design provisions for the operating phase Effective management of technical barriers in project development and design processes also need to address relevant dependencies with operational and organizational aspects for the operating phase. Some examples of interfaces between technical, operational and organizational aspects to be considered are: operational prerequisites for start-up and use; measures and restrictions that are necessary in the event of overriding, disconnection or in the event of missing/impaired safety systems and barriers; maintenance; competence; emergency preparedness; manual intervention. In order to ensure solutions which are suited for varying conditions, particular prerequisites shall be accommodated for in the design phase (and sustained during the operating phase). Examples of aspects that should be addressed are: assumptions including conditions and possible actions, when operating in different modes, i.e. normal, test, fault, failure, degraded. (Relevant assumptions in risk analyses should be according to requirements in the different installation specific performance standards); NORSOK S-001:2018 NORSOK © 2018 15 provisions, routines and logs for isolation of safety related functions during testing and maintenance, e.g. by inhibit (disabling input signal) and override (disabling output action). Such isolation should not render unnecessarily large parts of the system inactive. Logging, manual or automatic, of any such isolation action, e.g. time, number and duration, is mandatory; requirements for compensatory measures. (Responsible personnel for the operating phase will need to implement the necessary measures to remedy or compensate for non-conformities, missing or impaired barriers). The basis for inspection, testing and maintenance shall be described as part of project development in close liaison with the end user and be finalized before start-up. Important elements are: Systems, equipment and barriers shall be classified as regards the health, safety and environment consequences of potential functional failures. Information in performance standards shall regardless of other criticality analyses (e.g. according to NORSOK Z-008) be used as basis for categorizing safety critical equipment. An inspection-, testing- and maintenance programme for safety barriers shall be developed as part of project development. The programme should include test/inspection/maintenance methods and intervals. These shall be determined based upon regulatory requirements, company requirements, performance requirements, results/assumptions from analyses (e.g. SIL), criticality analysis (ref NORSOK Z-008), manufacturers™ recommendations, operating experience and relevant plant maintenance strategy. For instrumented safety systems, also see Norwegian Oil and Gas Association GL070. For structures, see NORSOK N-005. The safety functions/systems should, where reasonably practicable, allow for the required testing to be carried out without interrupting production or operations. Systems shall be established for monitoring barrier integrity, including possible deficiencies and degradation. The system should be established and populated with data during commissioning. Safety management during installation, start-up and the operating phases shall be defined in specific commissioning and operating procedures. This includes activity requirements and descriptions addressing: installation and commissioning manuals; start-up procedures. Verifying that relevant barrier elements meet all the specified performance requirements is the main objective in the commissioning phase. The commissioning test shall be performed under as realistic operating conditions as possible. Some tests, e.g. depressurisation systems or hydraulic power for ESD systems may have to be put through final capacity testing shortly after operations have started. The fire water system shall be subject to full scale dimensioning fire water demand scenario test, i.e. simultaneous release of all deluge skids covering the largest and largest neighbouring fire area. Relevant experience from commissioning and start-up shall be transferred to the operational phase. Safety related systems/functions required for safe project execution shall be operational to reflect the risk when the facility is gradually moved from construction to full operational status. Systems required for life support, communication, evacuation, fire detection, active and passive fire protection shall be operational when the facility is to be inhabited. NORSOK S-001:2018 16 NORSOK © 2018 The accidental loads/actions that can affect facilities or parts of facilities shall be determined. Also, the design loads that shall form basis for design and operation of facilities, systems and equipment need to be determined. Determination of design loads shall ensure that both deterministic and functional requirements in applicable regulations are met. The chosen design accidental loads that are to be used as basis for design shall ensure that facilities, systems and equipment are designed in such a way that relevant accidental situations will not result in unacceptable consequences. In addition to loads described in the subsequent sections, the following loads shall be included (ref. NORSOK N-003 Actions and action effects and NORSOK Z-013 Risk and emergency preparedness analysis); swinging/falling loads (e.g. impact loads to be absorbed without critical damage including subsea pipeline, risers and equipment), ship collisions (e.g. impact loads to be absorbed without critical damage including effects on wells and risers), and extreme environmental loads. Explosion loads from ignited gas clouds are strongly dependent on factors such as: cloud size and gas concentration; gas type; confinement and/or congestion of the affected area; explosion relief solutions; ignition location. Design explosion loads shall be established using a recognised method (e.g. NORSOK Z-013) and a representative geometric explosion model with representative equipment density. It is recognized that in the initial design the detail arrangement may not have been developed. An explosion study should be performed at an early stage, enabling the key installation parts to be located favorably with regard to explosion. The methods and detailing of the input will reflect this situation. Explosion loads shall be defined for relevant horizontal and vertical area dividers (pressure and impulse from explosion) and relevant equipment (pressure/drag forces). Explosion loads shall also be defined for areas external to the initial explosion location (typical LQ, utility modules etc.) if applicable. Equipment that can become a flying object and can significantly impair critical safety equipment/structures such as fire divisions, riser valves, wellheads, blowdown piping, should be considered secured. Examples of such equipment are well hatches, panels, temporary equipment, etc. The heat load from hydrocarbon fires is strongly dependent on: hydrocarbon composition and fire type (gas, liquid, jet, liquid spray or pool fire); fire size (optical thickness, velocity, turbulence and heat loss); NORSOK S-001:2018 NORSOK © 2018 17 geometry and ventilation conditions (turbulence, fuel/ventilation controlled, preheating of air, heat loss). For main load bearing structures, the heat load distribution is of great importance. A validated computational fluid dynamics (CFD) model shall be used to provide realistic modelling of the fire source and the effect of the surroundings in order to define the design accidental load. Care shall be taken when selecting simulation cases. Either these shall be selected and used conservatively, or a larger number of simulations are necessary to be statistically representative. The worst credible process fire (WCPF) in a fire area is derived from an ignited leak in the ESD-segment including possible escalation that will give the worst exposure of main load bearing structures and fire divisions with regard to duration (not related to the time needed for safe evacuation) and heat load distribution. ESD valves and emergency depressurization valves limiting the supply of fuel can be assumed to function. With respect to liquid spills, the open drain or grating in the area can be taken into account. The load from the WCPF shall be covered by the design accidental load for main load bearing structures and fire divisions. The identified WCPF shall not escalate to hydrocarbon pipeline risers or to wells (flow from reservoir) to avoid impairment of the main load bearing structures. Typical relevant scenarios would be: 1) a fire from the liquid segment giving the longest duration above critical rate related to main load bearing structures and fire divisions; 2) a jet fire from the largest gas EDP segment escalating to item 1 above. Relevant segments to be considered for WCPF are topside process segments limited by ESD valves. For wellhead areas, gas lift volumes in well annuli shall be included in the evaluation to determine the WCPF, unless the supply to the annulus is protected with a hydraulically activated integrated wellhead valve, i.e. with an ESD function, and there are no other leak points on the annulus that can give new critical leak rates, ref. also subclause 26.4. When assessing the WCPF, consequences of possible escalation to one other ESD segment (including the largest gas lift annulus volume unless protected as described above), shall be taken into account. Normally such escalation will not occur at the end of the fire under consideration and prolong this in a way affecting the worst exposure of the main load bearing structures and fire divisions. In most cases escalations will result in a large increase in the fire size in a certain time period, but normally not in a way that will affect the duration of the initial fire in a critical manner. 5.6.3.Unacceptable ruptures of process equipment in a fire situation. Rupture of process equipment in fire situations is unacceptable if this leads to one of the following: a fire duration and heat load distribution that is not covered by the design accidental load to protect structures and fire divisions. Ref. worst credible process fire; BLEVE (Boiling Liquid Expanding Vapor Explosion) Œ normally only relevant for volatile liquids such as propane; fatalities or serious injury in fire areas outside of the area of the initial event (fire) before escape to safe areas has been carried out; or NORSOK S-001:2018 18 NORSOK © 2018 impairment of main safety functions if incident frequencies exceed risk acceptance criteria, ref. NORSOK Z-013. In addition, ruptures that may lead to major economic losses may be defined as unacceptable. Each installation needs to define unacceptable ruptures based on these principles. In addition, the ALARP-principle is important and the best solution would be to avoid the risk of ruptures due to fires by all other means than passive fire protection due to e.g. reduced corrosion under insulation and inspection. The actual criteria will normally be expressed as: minimum time to rupture causing a certain release rate; o dependent on estimated time to escape from actual fire area and if an escalation has the possibility to hinder escape from other fire areas; max allowed pressure at time of rupture for piping and vessels (normally different); o important for pressure shock effects, missile effects from vessels and recoil effects from pipes; o dependent on layout, size of area and possibility for impairment of muster areas and hindering of evacuation; max allowed release rate, important for; o impairment of escape routes; o exposure of neighbouring areas and hence fire spread; o impairment of muster areas and evacuation means; will normally be different at different times after start of fire; dependent on; o layout, size of area and possibility for impairment of muster areas and hindering of evacuation; o released mass (duration) and fire protection of the surroundings. Typical minimum values for the above criteria are suggested below. These values shall be carefully considered for the actual use (i.e. for the specific installation), and modified as needed based on the given principles. If any emergency action can lead to the presence of personnel close to the fire, this shall be taken into account. Safe escape of personnel that will have to pass the fire, e.g. personnel in the far end or personnel involved in well securing (closure of well valves and/or BOP) during well interventions shall be accommodated for. Typical minimum values; Vessels o Not allowed to rupture before 10 minutes after start of the initial fire. o Not allowed to rupture before internal pressure is below 4.5 barg. Pipes o Instantaneous release shall not prevent all escape possibilities for personnel anywhere on the installation to reach Muster Areas. o Hydrocarbon release rate from any one escalation caused by a small jet fire (250 kW/m2) shall not exceed 2 kg/s until personnel have escaped the area of the fire. Typical time for escape from an area of the fire is 2 minutes. For areas difficult to get out of, this time shall be prolonged. o Hydrocarbon release rate from any one escalation caused by fires larger than 2 kg/s, shall not exceed the initial fire size until personnel have escaped the area of the fire. o In early screening work, larger fires can be represented with 350 kW/m2 and should not escalate with more than 5 kg/s. o For the first two minutes after escape from the area of the fire, gas release rate from any escalation shall not exceed 10 kg/s to accommodate safe escape from all other areas (this rate will normally not impair all escape routes from other areas). NORSOK S-001:2018 NORSOK © 2018 19 o Hydrocarbon release rate from any escalation shall not exceed 100 kg/s (typical value to avoid excessive heat radiation and smoke impairment) until all personnel have reached the Muster Areas. It is recommended to standardise on tubing that has a design pressure of approximately twice the plant™s highest normal operating pressure to allow escape from the fire-affected area prior to rupture of tubing exposed to fire. 5.6.3.5 Process equipment and piping Œ fire calculations A simplified estimate of the temperature development of objects and/or process piping and equipment in a fire can be based on a heat balance equation for the surface of the object: qnet = s Tr+ h(Tf - Ts(t)) - s Ts(t)Where qnet net heat transfer to object (W/m2) s emissivity of the surface material (-) s absorptivity of the surface material (-) (equals to s emissivity) Stefan-Boltzmann™s constant = 5.67*10-8 (W/m2*K4) Tr' flame radiation temperature (K) Tf flame gas temperature (K) Ts(t) surface temperature of the material at time t (K) h convective heat transfer coefficient (W/m2K) The following assumptions are recommended: For steel surfaces, a value of 0,85 for s is recommended. For jet fires, a convective heat transfer coefficient (h) of 100 W/m2K is recommended. For other types of fires, a heat transfer coefficient of 30 W/m2K is recommended. The flame radiation temperature, Tr, can be set equal to the flame gas temperature, Tf, and selected to obtain the recommended heat flux for the chosen fire scenario. The total incident heat load on an object is here defined as: qin = Tr+ h(Tf Œ Tamb) Where Tamb Temperature of the surroundings (not influenced by fire) For estimation of the temperature development in objects exposed to fires the recommended values for this incident heat load (time and space dependent radiative and convective heat load from fire) are shown in Table 1. NORSOK S-001:2018 20 NORSOK © 2018 Table 1 Š Proposed Incident Heat Fluxes for fuel controlled fires exposing pressurised process systems (no Credit for Water Deluge has been included in the table) Jet / Liquid spray firea) Pool fire a) For leak rates m > 2 kg/s For leak rates m > 0,1 kg/s Burning rate m > 2 kg/s Burning rate m > 0,1 kg/s Local peak heat load 350 kW/m2 250 kW/m2 250 kW/m2 150 kW/m2 Global average heat load 100 kW/m2 b) Notes a The heat flux will vary during the fire duration, and the values in this table are used as the average incident heat flux b The global average heat load of 100 kW/m2 is to be used for fire exposed area only as long as the leakage rate and burning rate is above 2 kg/s (for jet fires, same duration as 350 kW/m2 peak load). To use this load for the whole segment is generally considered conservative. Smaller areas receiving this load may be used provided it can be properly documented. This can be done by comparing realistic flame sizes with the extension of the segment under consideration, or for instance by using realistic fire simulations. See Figure 2. In addition to heat load level, the exposure duration is very important for the consequences from fires. The duration is dependent on ESD segment size and content, time to shutdown, time to start depressurisation, depressurisation rate and leak rate. When calculating if and when process segments will rupture due to jet fire exposure due to material weakening, the heat exposure from a leak should be evaluated by assessing two representative points in the fire as follows: Point 1: Using the maximum duration of a leak rate from any ESD segment in the area above 2 kg/s as the duration with local peak heat load of 350 kW/m2 (representing a point at some distances from the leak). Point 2: Using the maximum duration of a leak rate above 0,1 kg/s as the duration with local peak heat load of 250 kW/m2 (representing a point close to the leak). NOTE For calculation purposes it is assumed that the equipment has not been exposed to heat loads from point 1. Figure 2 Š Jet fire calculation The same principle applies for pool fires, but with different fire loads, ref. Table 1. This will determine the heating up of the metal of the most exposed parts of the segments, and hence the weakening of the material. NORSOK S-001:2018 NORSOK © 2018 21 The global average heat load is used as an input to the depressurisation calculations including the effect of boiling and vapour expansion of the segment inventory. Technology that requires qualification is defined as systems or components for which an acceptable reliability is not demonstrated by a documented track record for the particular application. The technology shall be qualified following a systematic approach, such as laid down in DNV-RP-A203 [1] or similar guideline, in order to demonstrate that it meets specified functional requirements and reliability targets. To ensure transfer of technical safety experience from relevant installations in operation, experience transfer activities should be part of the project development process. Sources of experience should include operational experience of relevant installations, project execution of relevant installations and modification to these, good technical solutions, solutions/equipment to be avoided. Temporary equipment shall be in accordance with NORSOK Z-015 Temporary Equipment and follow the relevant principles of this document, e.g. survivability of safety critical equipment and ignition source control. For temporary equipment operated as self-contained units, well completion and workover units etc, the interfaces shall be considered in the design phase both for normal and emergency situations, e.g., available power to secure operations in emergency situations and ignition source control. Main lay-down areas should be prepared for connection of containers and temporary equipment to the platform™s Fire & Gas system. The following safety documents should be developed during development of a new installation and be kept updated during the lifetime of the installation: Risk assessments (HAZID, HAZOP, risk analysis, risk evaluations, etc.); documentation which may include the Fire and Explosion Strategy (FES) and Escape Evacuation and Rescue Strategy (EER Strategy), also see subclause 5.2.6 Safety Strategy; Safety performance requirements which may be grouped in Safety Performance Standards; Safety system specifications and philosophies (supporting the Safety Strategy); Fire water report; Flare report; Design accidental load specification; Risk analyses and evaluations, including but not limited to: o survivability analyses for safety systems and barriers under the emergency conditions (scenarios and loads) which might be present when it is required to fulfil its role; o ESD Valve sectionalisation and if applicable other valves that have a role in an ESD situation, e.g. check valves; o reliability and availability; o fire load analyses; o explosion analyses; NORSOK S-001:2018 22 NORSOK © 2018 o dispersion analyses; o local vents; o PFP requirement and Fire integrity analysis; Safety arrangements documentation, drawings and diagrams as follows: o Fire and blast divisions; o Penetration dossier for fire divisions; o Structural passive fire protection; o Area classification; o Fire and gas detection layout; o Fire Protection Data Sheets (FPDS) (see example in Annex B)/ Area Safety Charts / F&G cause and effect (C&E) diagrams; o Escape routes, muster areas, areas for first aid treatment; o Safety equipment plot plans; o Active firefighting (plot plans and P&IDs); o P&IDs and Process safety analysis tables (SAT); o PSD/ESD cause and effect (C&E) diagrams; ESD shutdown hierarchy; SRS for instrumented safety systems. Safety interface documentation shall be produced where relevant in order to ensure that safety requirements are addressed and implemented in the development of the design and between different contractors and installations, e.g. subsea installation, storage units and fixed platforms. 6
96 | 6 Layout
97
98
99 | and part 29), Explosive atmospheres IEC 60331(all parts), Tests for electric cables under fire conditions Œ Circuit integrity IEC 61508(all parts), Functional safety of electrical/electronic/programmable electronic safety-related systems IEC 61511(all parts), Functional safety Œ Safety instrumented systems for the process industry sector IEC 61892(parts 1, 2, 3, 5, 6:2013 and 7) Mobile and fixed offshore units Œ Electrical installations API RP 14C:2017, Recommended Practice for Analysis, Design, Installation, and Testing of Basic Surface Safety Systems for Offshore Production Platforms (8th ed) API Spec 17J, Specification for Unbonded Flexible Pipe API STD 520, Sizing, Selection, and Installation of Pressure-relieving Devices API STD 521, Pressure-Relieving and Depressurizing Systems Directive 94/9/EC, Concerning equipment and protective systems intended for use in potentially explosive atmospheres (ATEX ﬁProductﬂ) DNVGL-ST-E406, Design of Free Fall Lifeboats DNVGL-ST-F201, Dynamic risers NORSOK S-001:2018 NORSOK © 2018 3 EEMUA 191 Alarm systems - a guide to design, management and procurement EI 15, Model code of safe practice Part 15: Area classification code for installations handling flammable fluids LSA Code, IMO SOLAS Life saving appliances (LSA) Code, adopted by the Maritime Safety Committee by resolution MSC.48 (66) Norwegian Oil and Gas Association GL064, Anbefalte retningslinjer for etablering av områdeberedskap Norwegian Oil and Gas Association GL070, Guidelines for the Application of IEC 61508 and IEC 61511 in the petroleum activities on the continental shelf Norwegian Oil and Gas Association GL075, Anbefalte retningslinjer for vannbaserte brannbekjempelsessystemer Norwegian Oil and Gas Association GL094, Kravspesifikasjoner for redningsdrakt til bruk på norsk kontinentalsokkel. MODU Code, Code for the construction and equipment of mobile offshore drilling units NFPA 11, Standard for Low-, Medium-, and High-Expansion Foam NFPA 13, Installation of Sprinkler Systems NFPA 14, Standard for the Installation of Standpipe and Hose Systems NFPA 15, Standard for Water Spray Fixed Systems for Fire Protection NFPA 16, Standard for the Installation of Foam-Water Sprinkler and Foam-Water Spray Systems NFPA 20, Standard for the Installation of Stationary Fire Pumps for Fire Protection Spray Systems NFPA 750, Standard on Water Mist Fire Protection Systems NMA Regulations No.67, Regulation concerning ballast systems on mobile offshore units (Ballast Regulations) NMA Regulations No. 90, Evacuation and Life-saving appliances on mobile offshore units NMA Regulations No. 123, Regulation for mobile offshore units with production plants and equipment NMA Regulations No. 998, Regulation concerning positioning and anchoring systems on mobile offshore units For the purposes of this NORSOK standard, the following terms, definitions and abbreviations apply. 3.1 shall (requirement) expression in the content of a document conveying objectively verifiable criteria to be fulfilled and from which no deviation is permitted if compliance with the document is to be claimed Note 1 to entry: Requirements are expressed using the verbal forms specified in ISO/IEC Directives, Part 2 clause 7.2 Table 3. 3.2 should (recommendation) expression in the content of a document conveying a suggested possible choice or course of action deemed to be particularly suitable without necessarily mentioning or excluding others NORSOK S-001:2018 NORSOK © 2018 Note 1 to entry: Recommendations are expressed using the verbal forms specified in ISO/IEC Directives, Part 2 clause 7.3 Table 4. Note 2 to entry: In the negative form, a recommendation is the expression that a suggested possible choice or course of action is not preferred but it is not prohibited. 3.3 may (permission) expression in the content of a document conveying consent or liberty (or opportunity) to do something Note 1 to entry: Permissions are expressed using the verbal forms specified in ISO/IEC Directives Part 2 clause 7.Table 5. 3.can (possibility and capability) 1: expression in the content of a document conveying expected or conceivable material, physical or causal outcome. 2: expression in the content of a document conveying the ability, fitness, or quality necessary to do or achieve a specified thing Note 1 to entry: Possibility and capability is expressed using the verbal forms specified in in ISO/IEC Directives, Part 2 clause 7.5 Table 6. 3.5 area classification division of an installation into hazardous areas and non-hazardous areas and the sub-division of hazardous zones under normal operation. Note 1 to entry: Normal operation is a situation when the plant is operating within its design parameters. Minor releases of flammable material may be part of normal operation. For example, releases from seals that rely on wetting by the fluid being pumped are considered to be minor releases. Failures (such as breakdown of pump seals, flange gaskets or spillage caused by accidents) that involve repair or shutdown are not considered to be part of normal operation, and may require special precautions of potential ignition sources. 3.6 design accidental load accidental load/action used as a basis for design Note 1 to entry: The design load/action can be the same as the dimensioning accidental load/action, but it can be higher, based on different input and assessments such as ALARP, minimum requirements in the regulations etc. 3.7 design fire the design fire for load bearing structures and fire divisions includes as a minimum: the dimensioning fire worst credible process fire fire class requirements, e.g. H-class 3.8 detection area area, or areas, of similar environmental and operating conditions and hazards, and with similar detection and protection arrangements. NORSOK S-001:2018 NORSOK © 2018 5 Note 1 to entry: For HC areas, the detection area is normally similar to the fire area in question. Very large fire areas may exceptionally be split into two or more detection areas, e.g. large tank decks on FPSOs. Each detection area will have a C&E Diagram, e.g. FPDS. 3.9 dimensioning accidental load an accidental load/action that a function or a system shall be able to withstand for a given period of time to meet the defined acceptance criteria for risk 3.10 dimensioning gas cloud the minimum stoichiometric gas cloud which, when ignited, can create an explosion resulting in an explosion pressure exceeding the dimensioning explosion load of the area 3.11 escape route route from an area of an installation leading to a muster or embarkation area. 3.12 essential equipment equipment that shall be kept alive to maintain production or drilling/well operations. Note 1 to entry: Such equipment may include main power generator, main electrical distribution panels, diesel engines, heaters, boilers ventilation systems, unless defined as a safety critical item 3.13 evacuation planned method of leaving the installation in an emergency situation 3.1evaluation a simplified assessment which does not require to be documented in a separate analysis or study report Note 1 to entry: The reasoning and conclusions should be described e.g. in the safety strategy. 3.15 explosion load the load generated by combustion of a flammable gas or mist which generates pressure and drag effects 3.16 fire area area separated from other areas either by physical barriers (fire/blast division) or sufficient distance which will prevent a fire or explosion to spread to another fire area when exposed to the design loads. 3.17 fire load time and space dependent radiative and convective heat load from a fire 3.18 fire water (FW) pump system total system which supplies water for firefighting system Note 1 to entry: i.e. water inlets with filters, FW pumps, risers, power sources, power transmissions, fuel pipes/tanks and control systems NORSOK S-001:2018 6 NORSOK © 2018 3.19 hazardous area an area in which a flammable atmosphere is or may be expected to be present in quantities such as to require special precautions for the control of potential ignition sources 3.20 ignition Source equipment and activities which may under certain circumstances cause ignition of an explosive atmosphere Note 1 to entry: Typically ignition sources relate to the following type of equipment; non Ex-certified electrical equipment (or not approved for Zone 2), open flames, direct heat and hot surfaces, rotating machinery and combustion engines, mechanical sparks, static electricity, radio frequency energy, chemical reaction (e.g. iron sulphide). Note 2 to entry: Electrical equipment will not constitute an ignition source if in compliance with relevant IEC zone requirements or better. 3.21 ignition source groups Group 1 (non-essential equipment): non-explosion protected equipment which is not affecting production availability or safety integrity. Group 2 (essential equipment): non-explosion protected equipment which shall be kept alive to maintain production and drilling operation. Group 3 (safety critical equipment): non-explosion protected equipment that shall be in operation to ensure rescue and medical treatment of injured personnel, escape and evacuation, prevent escalation or bring the installation to a safe state. 3.22 inhibit disabling of the safety instrumented function input and prevention of a shutdown action; Note 1 to entry: e.g. by disabling of the input signal to the shutdown logic while still presenting the alarm to the operator 3.23 intermittently manned work area or work place where inspection, maintenance or other work is planned to last at least 2 h, but less than 8 h a day for at least 50 % of the installation™s operation time 3.2local equipment room (LER a room containing electrical and instrumentation equipment 3.25 main area area that includes similar functions on the installation. Note 1 to entry: Main areas can be the: a) living quarter b) utility area c) drilling area d) wellhead area e) process area f) storage area for hydrocarbons Note 2 to entry: Drilling and wellhead area may be combined. See subclause 20.4.1. NORSOK S-001:2018 NORSOK © 2018 7 3.26 muster area designated area where mustering shall take place in the event of general and/or evacuation alarm, and where personnel is sheltered while emergency response and evacuation pre-planning are undertaken 3.27 non-essential equipment any equipment not affecting production availability or safety integrity 3.28 non-hazardous area all areas not classified as hazardous under normal operation 3.29 normally not manned area work area or work place that is not permanently or intermittently manned. 3.30 normally not manned installations installations that can be left unmanned and still maintain their intended function through remote control 3.31 override disabling of the safety instrumented function output and prevention of a shutdown action, e.g. by disabling the signal from shutdown logic to an individual shutdown output action. 3.32 permanently manned work area or work place manned at least 8 hours a day for at least 50 % of the installations operation time 3.33 safety critical equipment equipment that shall be in operation to ensure rescue and medical treatment of injured personnel, escape and evacuation, prevent escalation or bring the installation to a safe state, Note 1 to entry: e.g. equipment powered from UPS and/or emergency generator(s), fire water pump drivers, etc. Ignition source Group 3, see definition, is a sub-group of this equipment. 3.3well barrier envelope of one or several barrier elements preventing well fluids from flowing unintentionally from the formation into another formation or to surface. For this document, the following abbreviations apply. AC/h air changes per hour AFP active fire protection AIS automatic identification system API American Petroleum Institute NORSOK S-001:2018 8 NORSOK © 2018 APS abandon platform shutdown ASV annular safety valve ASME American Society of Mechanical Engineers ATEX Atmosphères Explosibles (forskrift om utstyr og sikkerhetssystem til bruk i eksplosjonsfarlig område) BOP blow out preventer C&E cause and effect CAP critical action panel CCR central control room DHSV down hole safety valve DIFFS deck integrated firefighting system EDP Emergency Depressurisation EER evacuation, escape and rescue EN European Standard ESD emergency shutdown F&G fire and gas FPDS fire protection data sheet FPSO floating production, storage and offloading FSU floating storage unit FW fire water HC hydrocarbon HMI human machine interface HVAC heating, ventilation and air conditioning IEC International Electrotechnical Commission IMO International Maritime Organisation IDLH Immediate Danger to Life and Health ISC ignition source control ISO International Organization for Standardization IR infrared LAHH level alarm high high (trip level) LCS loading computer system LEL lower explosive limit LELm lower explosive limit meters LER local equipment room LIR local instrument room LQ living quarter MCP manual call point MOB man over board NORSOK S-001:2018 NORSOK © 2018 9 MODU mobile offshore drilling unit MV master valve NA not applicable NFPA National Fire Protection Association NMA Norwegian Maritime Authority NNMI normally not manned installations PA public address PAGA public address and general alarm PFD probability of failure on demand PFP passive fire protection PSD process shutdown PSV pressure safety valve RIO Remote input/output SAS safety and automation system SIL safety integrity level SOLAS International Convention for the Safety of Life at Sea SSIV subsea isolation valve UHF ultra high frequency VDU visual display unit UPS uninterruptible power supply VHF very high frequency WV wing valve Technical safety management (loss prevention) in project development comprises activities to identify risks and to develop and document safety strategies and performance requirements for safety systems and barriers. These are iterative processes as the project develops and design matures. Necessary supporting documentation (e.g. studies, analysis and design reviews) shall be provided with due consideration for timely input to design and procurement processes. Concepts combining a jack-up drilling rig and a fixed installation require special consideration, ref. aspects described in Annex A - Jack-up/jacket constellations. A follow-up system shall be established that enables proper documentation, handling, follow-up and closeout of agreed actions and recommendations from the various studies and analyses in the project. In the event space is allocated for future expansions in new project developments, the design should incorporate sufficient flexibility to include capacity for the additional equipment, e.g. fire water, flare etc. fire water. NORSOK S-001:2018 10 NORSOK © 2018 For modification projects (e.g. upgrading of existing installation/module, tie-in of satellite field), technical safety management activities adjusted to project scope and complexity shall be performed, including new analyses or updating of existing analyses for factors that are affected by the modification. The individual project or installation shall perform specific hazard identification and risk analysis and evaluation processes. Based on this process, the requirements in this document shall be supplemented as necessary to manage the risk. 5.2 A flow diagram illustrating some of the main activities related to technical safety design is shown in Figure 1. The activities are detailed in the immediate following subclauses. Reference is made to NORSOK Z-013 for details related to risk assessment. Figure 1 Š Context needs to be defined and compiled so that frame conditions, limitations and ambitions for the installation (and its areas and activities) are available for relevant personnel involved in technical safety issues or technical safety management. Examples of context are legislation, standards (internal/ external), concept decisions, operating conditions, prerequisites for use, assumptions/ requirements and NORSOK S-001:2018 NORSOK © 2018 11 demands to risk reduction. The context applied for the management of technical safety has to be traceable and documented. A major part of the context will be defined early in the development of an installation. During the installation life cycle the context will provide a basis for use/ reassessment and it need to be updated to ensure that all relevant changes and modifications are included. The starting point for the risk assessment is to identify hazards and their accidental events that are relevant for the design and operation of the installation. Within management of technical safety, various hazard identifications need to be performed. The structure of HAZIDs should preferably be area based, but for some cases they may also be a HAZID node (e.g. part of well, process or utility systems), phase or operational based. Based on hazard identifications it shall be possible to present an overview of possible hazards and accidental events that can occur in different areas and during different activities. The level of detail and depth of hazard identification will be dependent of the maturity of the projects. Risk and safety analyses / studies shall be performed to establish sufficiently detailed information about the risk associated with the identified hazards and accidental events. The information will be used to evaluate the risk and to decide which solutions (barriers), and related requirements that are needed for preventing, controlling and mitigating the hazards in addition to generic requirements given by the context. Evaluation of risk includes an assessment of: compliance with predefined evaluation criteria (e.g. minimum requirements and acceptance criteria in context); necessary ALARP processes to demonstrate that risk has been reduced to a level as low as reasonably practicable; uncertainties associated with the hazards, accidental events and their consequences as well as the risk reducing effect of the barriers. The results from risk analyses are used for many purposes. One is to provide information and decision support related to the need for and role of risk reducing measures (barriers) and their required performance. Another is to provide decision support regarding the risk level assessed and if this is considered acceptable for the facility. Reference is made to subclause 5.10 for examples of studies and evaluations. For a development project, the degree of details in the risk and safety analyses / studies will increase as the project matures through different phases. Thus, solutions, assumptions and conservative estimates typically used in early stages may be verified or changed due to more detailed analyses. The need for barrier functions shall be established based on the context, identified hazards and accidental events, risk analyses and risk evaluation activities. shall be prepared so that it is possible to identify the need for barrier functions in each installation area or relevant HAZID node. When the need for barrier functions are identified, systems and elements necessary for realizing the barrier functions shall be defined. Technical barriers often require some form of monitoring, control or activation by people to function as intended. Depending on the characteristics of the facility and its risk picture, different levels of automation may also be chosen for certain safety systems. Therefore, operational and emergency situation considerations shall be an integral part of technical barrier process. As part of project development, safety system design shall include a human factors study amongst others documenting the following: Identification of safety critical tasks (ﬁoperational barrier elementsﬂ) required for the safety system to function. These include tasks related to start-up, monitoring, operation, incident response and recovery in the event of technical failure. Description of performance requirements. These include who is responsible for performing a task, under what circumstances it is expected to be performed, available response time and how it shall be carried out. The results from the study shall be used as input to design, as well as preparations for operations. Input to design should include HMI and alarm system specifications, levels of automation, equipment labelling, system capacities and tolerances. This standard focuses on technical design requirements and addresses operational and organizational aspects supplementing the technical barriers. shall be prepared to record how specific hazards or accidental events are managed by the use of barrier functions, systems and elements. This documentation can be denoted the 'safety strategy™ (or ‚the barrier strategy™) and can replace the need for Fire and Explosion Strategy (FES) and the Escape, Evacuation and Rescue Strategy (EER strategy) as required by ISO 13702. do not necessarily need to be described in a single document. The strategy may be described and included in other relevant documentation where this is natural and appropriate. The need to develop separate strategies can be viewed in relation to the other documentation which exists or is prepared for the individual facility. Safety strategy documentation should also be prepared to outline applicable overall principles for design, layout, arrangement, philosophies and other high-level design and operational aspects related to barriers; e.g.: how different safety documentation are linked together; risk reduction principles - inherent safety design; premises for design; design provisions for the operating phase; accidental loads and resistance. Verifiable performance requirements shall be established to ensure that the barrier function is fulfilled. In some situations, performance requirements can also be set directly to barrier functions. Performance requirements shall be established as an integrated part of the design and construction process, as the decisions on what safety systems and barriers to install and their corresponding specifications are made. Performance requirement (PR) for technical barrier elements can be divided into the following categories: Functionality i.e. the ability of the barrier or barrier element to execute the objectives (intended role) affecting the progress of an accident, e.g. by ensuring capacity and effectiveness. The NORSOK S-001:2018 NORSOK © 2018 13 minimum functional requirement of barrier/barrier element is often given by regulations, referred standards and company internal requirements. However, the specific safety strategy can call for stricter or more nuanced requirements. Integrity of the barrier/barrier element, i.e. the barrier / barrier element™s ability to be present when needed (reliability and availability). These requirements can be determined based on specific safety analysis-/studies or the implementation of generic minimum requirements. The following general requirements apply: o Design and realisation, inclusive of relevant operating issues, of all safety instrumented systems (SIS) shall be based upon the principles of IEC 61508/IEC 61511. The minimum requirements presented in Norwegian Oil and Gas Association GL070 may be used instead of a full safety analysis/risk assessment for standardised solutions. o The applicable safety system, or affected parts of it, shall be designed to fail-to-safe principle, whereby the system goes to a predefined safe state in the event of detectable malfunction. It shall be designed with the aim of avoiding single defects / failures that may prohibit safety actions being executed. If it is not feasible to implement a fail-to-safe principle, an equivalent level of safety shall be achieved by redundancy and/or diagnostics and fault alarm to relevant manned control room. o The probability of single defects / failures causing inadvertent trip actions shall be as low as reasonably practicable (e.g. provide fault tolerance by means of automatic diagnostic features and redundancy). o All barriers or parts thereof, shall be protected against or withstand environmental conditions that may compromise their safety functions, e.g. ice, snow, sand, water, etc. Survivability of the barrier/barrier element, i.e. its ability to function under relevant accident scenarios and loads. Equipment with a safety function, during and after the accident, should be located so that the possible impact from accidental loads is minimised. To develop the survivability requirements, the design loads that shall form the basis for design of facilities, systems and equipment need to be determined, ref. subclause . Barriers/safety systems may be dependent on safety critical tasks to function, through e.g. monitoring, activation or control. For relevant safety systems, performance requirements should also be defined for operational / organizational barrier elements, ref. subclause 5.4. Each clause of this document from clause 6 and onwards describes generic design principles and requirements for the different safety systems and barriers. The installation specific performance requirements shall be developed based on this framework to manage the risk. It may be beneficial to group the various performance requirements into performance standards including a description of the role of the safety functions. Dependencies on and interfaces with other systems should also be described. A Safety Requirement Specification (SRS) is a documentation of requirements related to safety instrumented systems (SIS). The SRS documentation shall be developed during projects and shall provide the design basis for required SIS.ly, the SRS shall contain the relevant key information for use in specifying and operating the instrumented safety functions. However, the information required may be contained in other project documents referred to in the SRS, e.g. performance standards. Duplication of information should be avoided. The SRS shall contain three main types of requirements: NORSOK S-001:2018 1NORSOK © 2018 functional requirements such as capacities and response times, integrity requirements such as PFD and SIL, and, operating prerequisites and constraints. Further reference is given to IEC 61511 (Functional Safety Œ Safety Instrumented Systems for the process industry sectorﬂ) and Norwegian Oil and Gas Association GL070.. that needs to be developed to deepen or clarify performance requirements when necessary. Ref. subclause . Also, see Annex C for proposed format and information for data sheets for selected Safety Equipment. 5.3 Risk reduction principles and inherent safety design In concept development, priority shall be given to solutions that are inherently safe. If the hazard cannot be eliminated, probability reducing measures should be given priority over consequence reducing measures. The objectives of risk reduction principles and inherent safety design are to: eliminate or reduce potential hazards/increase inherent safety by; reduction, e.g. reducing the hazardous inventories or the frequency or duration of exposure; substitution, e.g. substituting hazardous materials with less hazardous ones; attenuation (moderation), e.g. using the hazardous materials or processes in a way that limits their hazard potential; simplifications, e.g. making the facility and process simpler to design, build and operate, hence less prone to equipment, control and human failure; reduce probability of hazardous events; establish mitigating measures, e.g. through safety barriers. The ALARP principle (As Low As Reasonable Practicable) shall be used to select the safety solutions. 5.Design provisions for the operating phase Effective management of technical barriers in project development and design processes also need to address relevant dependencies with operational and organizational aspects for the operating phase. Some examples of interfaces between technical, operational and organizational aspects to be considered are: operational prerequisites for start-up and use; measures and restrictions that are necessary in the event of overriding, disconnection or in the event of missing/impaired safety systems and barriers; maintenance; competence; emergency preparedness; manual intervention. In order to ensure solutions which are suited for varying conditions, particular prerequisites shall be accommodated for in the design phase (and sustained during the operating phase). Examples of aspects that should be addressed are: assumptions including conditions and possible actions, when operating in different modes, i.e. normal, test, fault, failure, degraded. (Relevant assumptions in risk analyses should be according to requirements in the different installation specific performance standards); NORSOK S-001:2018 NORSOK © 2018 15 provisions, routines and logs for isolation of safety related functions during testing and maintenance, e.g. by inhibit (disabling input signal) and override (disabling output action). Such isolation should not render unnecessarily large parts of the system inactive. Logging, manual or automatic, of any such isolation action, e.g. time, number and duration, is mandatory; requirements for compensatory measures. (Responsible personnel for the operating phase will need to implement the necessary measures to remedy or compensate for non-conformities, missing or impaired barriers). The basis for inspection, testing and maintenance shall be described as part of project development in close liaison with the end user and be finalized before start-up. Important elements are: Systems, equipment and barriers shall be classified as regards the health, safety and environment consequences of potential functional failures. Information in performance standards shall regardless of other criticality analyses (e.g. according to NORSOK Z-008) be used as basis for categorizing safety critical equipment. An inspection-, testing- and maintenance programme for safety barriers shall be developed as part of project development. The programme should include test/inspection/maintenance methods and intervals. These shall be determined based upon regulatory requirements, company requirements, performance requirements, results/assumptions from analyses (e.g. SIL), criticality analysis (ref NORSOK Z-008), manufacturers™ recommendations, operating experience and relevant plant maintenance strategy. For instrumented safety systems, also see Norwegian Oil and Gas Association GL070. For structures, see NORSOK N-005. The safety functions/systems should, where reasonably practicable, allow for the required testing to be carried out without interrupting production or operations. Systems shall be established for monitoring barrier integrity, including possible deficiencies and degradation. The system should be established and populated with data during commissioning. Safety management during installation, start-up and the operating phases shall be defined in specific commissioning and operating procedures. This includes activity requirements and descriptions addressing: installation and commissioning manuals; start-up procedures. Verifying that relevant barrier elements meet all the specified performance requirements is the main objective in the commissioning phase. The commissioning test shall be performed under as realistic operating conditions as possible. Some tests, e.g. depressurisation systems or hydraulic power for ESD systems may have to be put through final capacity testing shortly after operations have started. The fire water system shall be subject to full scale dimensioning fire water demand scenario test, i.e. simultaneous release of all deluge skids covering the largest and largest neighbouring fire area. Relevant experience from commissioning and start-up shall be transferred to the operational phase. Safety related systems/functions required for safe project execution shall be operational to reflect the risk when the facility is gradually moved from construction to full operational status. Systems required for life support, communication, evacuation, fire detection, active and passive fire protection shall be operational when the facility is to be inhabited. NORSOK S-001:2018 16 NORSOK © 2018 The accidental loads/actions that can affect facilities or parts of facilities shall be determined. Also, the design loads that shall form basis for design and operation of facilities, systems and equipment need to be determined. Determination of design loads shall ensure that both deterministic and functional requirements in applicable regulations are met. The chosen design accidental loads that are to be used as basis for design shall ensure that facilities, systems and equipment are designed in such a way that relevant accidental situation
100 | 6.1 Role
101 | The layout and arrangement of an installation shall reduce probability and the consequences of accidents through location, separation and orientation of areas, equipment and functions. The layout can amongst other contribute to: minimize the possibility of hazardous accumulations and spread of both flammable liquids and gaseous hydrocarbons; minimize the probability of ignition; separate areas required to be non-hazardous from those designated as being hazardous; minimize the consequences of fire and explosions and thereby reduced escalation risk; facilitate effective emergency response; provide for adequate arrangements for escape and evacuation. 6.2
102 | 6.2 Interfaces
103
104
105
106 | 6.3 Required utilities
107
108
109
110 | 6.4 Functional requirements
111
112
113
114 | 6.4.1 Main design principles
115 | The installation(s) shall be oriented with respect to the dominant wind direction to minimize the likelihood of a gas release or smoke drifting towards the accommodation and primary evacuation means. The installation shall be divided into main areas (accommodation, utility, drilling, wellhead, process and hydrocarbon storage). The main areas shall be located and designed to minimize the risk to people, environment and assets. Main areas shall normally be separated by use of physical barriers as fire and blast divisions to prevent the escalation of an accident from one main area to another. The utility area should serve as a barrier between hazardous areas and LQ. For installations that are part of a complex, the impact from major accidents e.g. blowouts and riser fires on the neighbouring installations shall be assessed. Mitigating measures can be length of the bridge, radiation shielding, etc. Muster areas, accommodation, evacuation means and escape routes shall be located where they are least affected by fires and explosions. Safety systems shall be located or protected to ensure operation during relevant emergency conditions. Systems and equipment such as FW pump units, emergency generator(s) and switchboards, UPS, ESD/ F&G nodes, ballast and position keeping controls shall be located as safe as possible in the accommodation or utility area. The PSD node should be located in the same room as the ESD/F&G nodes, reference is made to subclause 10.5. CCR shall be located as safe as possible in the accommodation or utility area with easy and safe access to evacuation facilities. Equipment and piping containing hydrocarbons shall be located or protected to minimize consequences from dropped objects, crane boom fall and swinging loads etc. Ventilation inlets, including combustion air inlets, shall be located in a safe area with respect to accidental gas leakages, ref. subclause 17.4.6. Doors from non-hazardous rooms facing directly towards hazardous areas should be avoided. Doors bordering naturally ventilated areas shall be self-closing and conform to fire partition requirements. Non-hazardous rooms with doors or openings less than 3 m away from hazardous area should be avoided. Equipment enclosures, e.g. for noise suppression, shall be subject to special consideration with respect to required safety functions. Such consideration should include impacts to F&G detection, fire water, drain, ventilation (effect on explosion overpressure and source of ventilation - see 17.4.6), area classification, Ex category on components, access, entering of confined space, light fixtures etc. The equipment enclosures should be made as small as possible in order to avoid it becoming a separate detection/fire area.
116 | 6.4.2 Riser flow line area
117
118
119
120 | 6.4.3 Process area
121 | Fire and explosion assessments shall be performed along with the development of the layout to minimise the built-in escalation potential. This shall be ensured through the following principles: Equipment and piping containing high-pressure gas should be located in the upper decks above the module support frame or main hull. Liquid vessels should be located lower than gas equipment. Low-pressure equipment containing large amount of liquids should be located and arranged so that exposure to jet fires is minimised. Process vessels, process piping, pig launchers and receivers and other hydrocarbon containing equipment shall be protected from external impact (e.g. from dropped objects or missiles due to disintegration of rotating machinery) or as found required through analysis.
122 | 6.4.4 Well areas
123
124
125
126 | 6.4.5 Piping
127 | and valves NORSOK L-002, Piping design, layout and stress analysis NORSOK L-005, Compact flanged connections NORSOK N-001, Structural design NORSOK N-003, Actions and action effects NORSOK N-005, In-service integrity management of structures and maritime systems NORSOK P-002, Process System Design NORSOK R-002, Lifting Equipment NORSOK T-001, Telecom Systems NORSOK T-100, Telecom Subsystems NORSOK Z-008, Risk based maintenance and consequence classification NORSOK Z-013, Risk and emergency preparedness analysis NORSOK Z-015, Temporary Equipment NORSOK S-001:2018 2 NORSOK © 2018 CENELEC CLC/TR 50427, Assessment of inadvertent ignition of flammable atmospheres by radio-frequency radiation EN 5all parts, Fire Detection and Alarm Systems EN 403, Respiratory protective devices for self-rescue - Filtering devices with hood for escape from fire - Requirements, testing, marking EN 1127-1, Explosive atmospheres - Explosion prevention and protection - Part 1: Basic concepts and methodology EN 1838, Lighting applications Œ Emergency lighting EN 12266-1, Industrial valves - Testing of metallic valves - Part 1: Pressure tests, test procedures and acceptance criteria - Mandatory requirements EN 12266-2, Industrial valves - Testing of metallic valves - Part 2: Tests, test procedures and acceptance criteria - Supplementary requirements EN 62682 Management of alarms systems for the process industries ISO 10418:2003/AC:2009, Petroleum and natural gas industries Œ Offshore production installations Œ Basic surface process safety systems ISO 10423, Petroleum and natural gas industries - Drilling and production equipment - Wellhead and christmas tree equipment ISO 10497, Testing of valves - Fire type-testing requirements ISO 13702:2015, Petroleum and natural gas industries Œ Control and mitigation of fires and explosions on offshore production installations Œ Requirements and guidelines ISO 15138, Petroleum and natural gas industries - Offshore production installations - Heating, ventilation and air-conditioning ISO 16069, Graphical Symbols Œ Safety Signs -- Safety Way Guidance System (SWGS) ISO 22899, Determination of the resistance to jet fires of passive fire protection materials -- Part 1: requirements ISO 80079-36. Explosive atmospheres - Part 36: Non-electrical equipment for explosive atmospheres - Basic method and requirements IEC 60079(part 10, part 14:2013/COR1:201and part 29), Explosive atmospheres IEC 60331(all parts), Tests for electric cables under fire conditions Œ Circuit integrity IEC 61508(all parts), Functional safety of electrical/electronic/programmable electronic safety-related systems IEC 61511(all parts), Functional safety Œ Safety instrumented systems for the process industry sector IEC 61892(parts 1, 2, 3, 5, 6:2013 and 7) Mobile and fixed offshore units Œ Electrical installations API RP 14C:2017, Recommended Practice for Analysis, Design, Installation, and Testing of Basic Surface Safety Systems for Offshore Production Platforms (8th ed) API Spec 17J, Specification for Unbonded Flexible Pipe API STD 520, Sizing, Selection, and Installation of Pressure-relieving Devices API STD 521, Pressure-Relieving and Depressurizing Systems Directive 94/9/EC, Concerning equipment and protective systems intended for use in potentially explosive atmospheres (ATEX ﬁProductﬂ) DNVGL-ST-E406, Design of Free Fall Lifeboats DNVGL-ST-F201, Dynamic risers NORSOK S-001:2018 NORSOK © 2018 3 EEMUA 191 Alarm systems - a guide to design, management and procurement EI 15, Model code of safe practice Part 15: Area classification code for installations handling flammable fluids LSA Code, IMO SOLAS Life saving appliances (LSA) Code, adopted by the Maritime Safety Committee by resolution MSC.48 (66) Norwegian Oil and Gas Association GL064, Anbefalte retningslinjer for etablering av områdeberedskap Norwegian Oil and Gas Association GL070, Guidelines for the Application of IEC 61508 and IEC 61511 in the petroleum activities on the continental shelf Norwegian Oil and Gas Association GL075, Anbefalte retningslinjer for vannbaserte brannbekjempelsessystemer Norwegian Oil and Gas Association GL094, Kravspesifikasjoner for redningsdrakt til bruk på norsk kontinentalsokkel. MODU Code, Code for the construction and equipment of mobile offshore drilling units NFPA 11, Standard for Low-, Medium-, and High-Expansion Foam NFPA 13, Installation of Sprinkler Systems NFPA 14, Standard for the Installation of Standpipe and Hose Systems NFPA 15, Standard for Water Spray Fixed Systems for Fire Protection NFPA 16, Standard for the Installation of Foam-Water Sprinkler and Foam-Water Spray Systems NFPA 20, Standard for the Installation of Stationary Fire Pumps for Fire Protection Spray Systems NFPA 750, Standard on Water Mist Fire Protection Systems NMA Regulations No.67, Regulation concerning ballast systems on mobile offshore units (Ballast Regulations) NMA Regulations No. 90, Evacuation and Life-saving appliances on mobile offshore units NMA Regulations No. 123, Regulation for mobile offshore units with production plants and equipment NMA Regulations No. 998, Regulation concerning positioning and anchoring systems on mobile offshore units For the purposes of this NORSOK standard, the following terms, definitions and abbreviations apply. 3.1 shall (requirement) expression in the content of a document conveying objectively verifiable criteria to be fulfilled and from which no deviation is permitted if compliance with the document is to be claimed Note 1 to entry: Requirements are expressed using the verbal forms specified in ISO/IEC Directives, Part 2 clause 7.2 Table 3. 3.2 should (recommendation) expression in the content of a document conveying a suggested possible choice or course of action deemed to be particularly suitable without necessarily mentioning or excluding others NORSOK S-001:2018 NORSOK © 2018 Note 1 to entry: Recommendations are expressed using the verbal forms specified in ISO/IEC Directives, Part 2 clause 7.3 Table 4. Note 2 to entry: In the negative form, a recommendation is the expression that a suggested possible choice or course of action is not preferred but it is not prohibited. 3.3 may (permission) expression in the content of a document conveying consent or liberty (or opportunity) to do something Note 1 to entry: Permissions are expressed using the verbal forms specified in ISO/IEC Directives Part 2 clause 7.Table 5. 3.can (possibility and capability) 1: expression in the content of a document conveying expected or conceivable material, physical or causal outcome. 2: expression in the content of a document conveying the ability, fitness, or quality necessary to do or achieve a specified thing Note 1 to entry: Possibility and capability is expressed using the verbal forms specified in in ISO/IEC Directives, Part 2 clause 7.5 Table 6. 3.5 area classification division of an installation into hazardous areas and non-hazardous areas and the sub-division of hazardous zones under normal operation. Note 1 to entry: Normal operation is a situation when the plant is operating within its design parameters. Minor releases of flammable material may be part of normal operation. For example, releases from seals that rely on wetting by the fluid being pumped are considered to be minor releases. Failures (such as breakdown of pump seals, flange gaskets or spillage caused by accidents) that involve repair or shutdown are not considered to be part of normal operation, and may require special precautions of potential ignition sources. 3.design accidental load accidental load/action used as a basis for design Note 1 to entry: The design load/action can be the same as the dimensioning accidental load/action, but it can be higher, based on different input and assessments such as ALARP, minimum requirements in the regulations etc. 3.7 design fire the design fire for load bearing structures and fire divisions includes as a minimum: the dimensioning fire worst credible process fire fire class requirements, e.g. H-class 3.8 detection area area, or areas, of similar environmental and operating conditions and hazards, and with similar detection and protection arrangements. NORSOK S-001:2018 NORSOK © 2018 5 Note 1 to entry: For HC areas, the detection area is normally similar to the fire area in question. Very large fire areas may exceptionally be split into two or more detection areas, e.g. large tank decks on FPSOs. Each detection area will have a C&E Diagram, e.g. FPDS. 3.9 dimensioning accidental load an accidental load/action that a function or a system shall be able to withstand for a given period of time to meet the defined acceptance criteria for risk 3.10 dimensioning gas cloud the minimum stoichiometric gas cloud which, when ignited, can create an explosion resulting in an explosion pressure exceeding the dimensioning explosion load of the area 3.11 escape route route from an area of an installation leading to a muster or embarkation area. 3.12 essential equipment equipment that shall be kept alive to maintain production or drilling/well operations. Note 1 to entry: Such equipment may include main power generator, main electrical distribution panels, diesel engines, heaters, boilers ventilation systems, unless defined as a safety critical item 3.13 evacuation planned method of leaving the installation in an emergency situation 3.1evaluation a simplified assessment which does not require to be documented in a separate analysis or study report Note 1 to entry: The reasoning and conclusions should be described e.g. in the safety strategy. 3.15 explosion load the load generated by combustion of a flammable gas or mist which generates pressure and drag effects 3.1fire area area separated from other areas either by physical barriers (fire/blast division) or sufficient distance which will prevent a fire or explosion to spread to another fire area when exposed to the design loads. 3.17 fire load time and space dependent radiative and convective heat load from a fire 3.18 fire water (FW) pump system total system which supplies water for firefighting system Note 1 to entry: i.e. water inlets with filters, FW pumps, risers, power sources, power transmissions, fuel pipes/tanks and control systems NORSOK S-001:2018 NORSOK © 2018 3.19 hazardous area an area in which a flammable atmosphere is or may be expected to be present in quantities such as to require special precautions for the control of potential ignition sources 3.20 ignition Source equipment and activities which may under certain circumstances cause ignition of an explosive atmosphere Note 1 to entry: Typically ignition sources relate to the following type of equipment; non Ex-certified electrical equipment (or not approved for Zone 2), open flames, direct heat and hot surfaces, rotating machinery and combustion engines, mechanical sparks, static electricity, radio frequency energy, chemical reaction (e.g. iron sulphide). Note 2 to entry: Electrical equipment will not constitute an ignition source if in compliance with relevant IEC zone requirements or better. 3.21 ignition source groups Group 1 (non-essential equipment): non-explosion protected equipment which is not affecting production availability or safety integrity. Group 2 (essential equipment): non-explosion protected equipment which shall be kept alive to maintain production and drilling operation. Group 3 (safety critical equipment): non-explosion protected equipment that shall be in operation to ensure rescue and medical treatment of injured personnel, escape and evacuation, prevent escalation or bring the installation to a safe state. 3.22 inhibit disabling of the safety instrumented function input and prevention of a shutdown action; Note 1 to entry: e.g. by disabling of the input signal to the shutdown logic while still presenting the alarm to the operator 3.23 intermittently manned work area or work place where inspection, maintenance or other work is planned to last at least 2 h, but less than 8 h a day for at least 50 % of the installation™s operation time 3.2local equipment room (LER a room containing electrical and instrumentation equipment 3.25 main area area that includes similar functions on the installation. Note 1 to entry: Main areas can be the: a) living quarter b) utility area c) drilling area d) wellhead area e) process area f) storage area for hydrocarbons Note 2 to entry: Drilling and wellhead area may be combined. See subclause 20.4.1. NORSOK S-001:2018 NORSOK © 2018 7 3.2muster area designated area where mustering shall take place in the event of general and/or evacuation alarm, and where personnel is sheltered while emergency response and evacuation pre-planning are undertaken 3.27 non-essential equipment any equipment not affecting production availability or safety integrity 3.28 non-hazardous area all areas not classified as hazardous under normal operation 3.29 normally not manned area work area or work place that is not permanently or intermittently manned. 3.30 normally not manned installations installations that can be left unmanned and still maintain their intended function through remote control 3.31 override disabling of the safety instrumented function output and prevention of a shutdown action, e.g. by disabling the signal from shutdown logic to an individual shutdown output action. 3.32 permanently manned work area or work place manned at least 8 hours a day for at least 50 % of the installations operation time 3.33 safety critical equipment equipment that shall be in operation to ensure rescue and medical treatment of injured personnel, escape and evacuation, prevent escalation or bring the installation to a safe state, Note 1 to entry: e.g. equipment powered from UPS and/or emergency generator(s), fire water pump drivers, etc. Ignition source Group 3, see definition, is a sub-group of this equipment. 3.3well barrier envelope of one or several barrier elements preventing well fluids from flowing unintentionally from the formation into another formation or to surface. For this document, the following abbreviations apply. AC/h air changes per hour AFP active fire protection AIS automatic identification system API American Petroleum Institute NORSOK S-001:2018 8 NORSOK © 2018 APS abandon platform shutdown ASV annular safety valve ASME American Society of Mechanical Engineers ATEX Atmosphères Explosibles (forskrift om utstyr og sikkerhetssystem til bruk i eksplosjonsfarlig område) BOP blow out preventer C&E cause and effect CAP critical action panel CCR central control room DHSV down hole safety valve DIFFS deck integrated firefighting system EDP Emergency Depressurisation EER evacuation, escape and rescue EN European Standard ESD emergency shutdown F&G fire and gas FPDS fire protection data sheet FPSO floating production, storage and offloading FSU floating storage unit FW fire water HC hydrocarbon HMI human machine interface HVAC heating, ventilation and air conditioning IEC International Electrotechnical Commission IMO International Maritime Organisation IDLH Immediate Danger to Life and Health ISC ignition source control ISO International Organization for Standardization IR infrared LAHH level alarm high high (trip level) LCS loading computer system LEL lower explosive limit LELm lower explosive limit meters LER local equipment room LIR local instrument room LQ living quarter MCP manual call point MOB man over board NORSOK S-001:2018 NORSOK © 2018 9 MODU mobile offshore drilling unit MV master valve NA not applicable NFPA National Fire Protection Association NMA Norwegian Maritime Authority NNMI normally not manned installations PA public address PAGA public address and general alarm PFD probability of failure on demand PFP passive fire protection PSD process shutdown PSV pressure safety valve RIO Remote input/output SAS safety and automation system SIL safety integrity level SOLAS International Convention for the Safety of Life at Sea SSIV subsea isolation valve UHF ultra high frequency VDU visual display unit UPS uninterruptible power supply VHF very high frequency WV wing valve Technical safety management (loss prevention) in project development comprises activities to identify risks and to develop and document safety strategies and performance requirements for safety systems and barriers. These are iterative processes as the project develops and design matures. Necessary supporting documentation (e.g. studies, analysis and design reviews) shall be provided with due consideration for timely input to design and procurement processes. Concepts combining a jack-up drilling rig and a fixed installation require special consideration, ref. aspects described in Annex A - Jack-up/jacket constellations. A follow-up system shall be established that enables proper documentation, handling, follow-up and closeout of agreed actions and recommendations from the various studies and analyses in the project. In the event space is allocated for future expansions in new project developments, the design should incorporate sufficient flexibility to include capacity for the additional equipment, e.g. fire water, flare etc. fire water. NORSOK S-001:2018 10 NORSOK © 2018 For modification projects (e.g. upgrading of existing installation/module, tie-in of satellite field), technical safety management activities adjusted to project scope and complexity shall be performed, including new analyses or updating of existing analyses for factors that are affected by the modification. The individual project or installation shall perform specific hazard identification and risk analysis and evaluation processes. Based on this process, the requirements in this document shall be supplemented as necessary to manage the risk. 5.2 A flow diagram illustrating some of the main activities related to technical safety design is shown in Figure 1. The activities are detailed in the immediate following subclauses. Reference is made to NORSOK Z-013 for details related to risk assessment. Figure 1 Š Context needs to be defined and compiled so that frame conditions, limitations and ambitions for the installation (and its areas and activities) are available for relevant personnel involved in technical safety issues or technical safety management. Examples of context are legislation, standards (internal/ external), concept decisions, operating conditions, prerequisites for use, assumptions/ requirements and NORSOK S-001:2018 NORSOK © 2018 11 demands to risk reduction. The context applied for the management of technical safety has to be traceable and documented. A major part of the context will be defined early in the development of an installation. During the installation life cycle the context will provide a basis for use/ reassessment and it need to be updated to ensure that all relevant changes and modifications are included. The starting point for the risk assessment is to identify hazards and their accidental events that are relevant for the design and operation of the installation. Within management of technical safety, various hazard identifications need to be performed. The structure of HAZIDs should preferably be area based, but for some cases they may also be a HAZID node (e.g. part of well, process or utility systems), phase or operational based. Based on hazard identifications it shall be possible to present an overview of possible hazards and accidental events that can occur in different areas and during different activities. The level of detail and depth of hazard identification will be dependent of the maturity of the projects. Risk and safety analyses / studies shall be performed to establish sufficiently detailed information about the risk associated with the identified hazards and accidental events. The information will be used to evaluate the risk and to decide which solutions (barriers), and related requirements that are needed for preventing, controlling and mitigating the hazards in addition to generic requirements given by the context. Evaluation of risk includes an assessment of: compliance with predefined evaluation criteria (e.g. minimum requirements and acceptance criteria in context); necessary ALARP processes to demonstrate that risk has been reduced to a level as low as reasonably practicable; uncertainties associated with the hazards, accidental events and their consequences as well as the risk reducing effect of the barriers. The results from risk analyses are used for many purposes. One is to provide information and decision support related to the need for and role of risk reducing measures (barriers) and their required performance. Another is to provide decision support regarding the risk level assessed and if this is considered acceptable for the facility. Reference is made to subclause 5.10 for examples of studies and evaluations. For a development project, the degree of details in the risk and safety analyses / studies will increase as the project matures through different phases. Thus, solutions, assumptions and conservative estimates typically used in early stages may be verified or changed due to more detailed analyses. The need for barrier functions shall be established based on the context, identified hazards and accidental events, risk analyses and risk evaluation activities. shall be prepared so that it is possible to identify the need for barrier functions in each installation area or relevant HAZID node. When the need for barrier functions are identified, systems and elements necessary for realizing the barrier functions shall be defined. Technical barriers often require some form of monitoring, control or activation by people to function as intended. Depending on the characteristics of the facility and its risk picture, different levels of automation may also be chosen for certain safety systems. Therefore, operational and emergency situation considerations shall be an integral part of technical barrier process. As part of project development, safety system design shall include a human factors study amongst others documenting the following: Identification of safety critical tasks (ﬁoperational barrier elementsﬂ) required for the safety system to function. These include tasks related to start-up, monitoring, operation, incident response and recovery in the event of technical failure. Description of performance requirements. These include who is responsible for performing a task, under what circumstances it is expected to be performed, available response time and how it shall be carried out. The results from the study shall be used as input to design, as well as preparations for operations. Input to design should include HMI and alarm system specifications, levels of automation, equipment labelling, system capacities and tolerances. This standard focuses on technical design requirements and addresses operational and organizational aspects supplementing the technical barriers. shall be prepared to record how specific hazards or accidental events are managed by the use of barrier functions, systems and elements. This documentation can be denoted the 'safety strategy™ (or ‚the barrier strategy™) and can replace the need for Fire and Explosion Strategy (FES) and the Escape, Evacuation and Rescue Strategy (EER strategy) as required by ISO 13702. do not necessarily need to be described in a single document. The strategy may be described and included in other relevant documentation where this is natural and appropriate. The need to develop separate strategies can be viewed in relation to the other documentation which exists or is prepared for the individual facility. Safety strategy documentation should also be prepared to outline applicable overall principles for design, layout, arrangement, philosophies and other high-level design and operational aspects related to barriers; e.g.: how different safety documentation are linked together; risk reduction principles - inherent safety design; premises for design; design provisions for the operating phase; accidental loads and resistance. Verifiable performance requirements shall be established to ensure that the barrier function is fulfilled. In some situations, performance requirements can also be set directly to barrier functions. Performance requirements shall be established as an integrated part of the design and construction process, as the decisions on what safety systems and barriers to install and their corresponding specifications are made. Performance requirement (PR) for technical barrier elements can be divided into the following categories: Functionality i.e. the ability of the barrier or barrier element to execute the objectives (intended role) affecting the progress of an accident, e.g. by ensuring capacity and effectiveness. The NORSOK S-001:2018 NORSOK © 2018 13 minimum functional requirement of barrier/barrier element is often given by regulations, referred standards and company internal requirements. However, the specific safety strategy can call for stricter or more nuanced requirements. Integrity of the barrier/barrier element, i.e. the barrier / barrier element™s ability to be present when needed (reliability and availability). These requirements can be determined based on specific safety analysis-/studies or the implementation of generic minimum requirements. The following general requirements apply: o Design and realisation, inclusive of relevant operating issues, of all safety instrumented systems (SIS) shall be based upon the principles of IEC 61508/IEC 61511. The minimum requirements presented in Norwegian Oil and Gas Association GL070 may be used instead of a full safety analysis/risk assessment for standardised solutions. o The applicable safety system, or affected parts of it, shall be designed to fail-to-safe principle, whereby the system goes to a predefined safe state in the event of detectable malfunction. It shall be designed with the aim of avoiding single defects / failures that may prohibit safety actions being executed. If it is not feasible to implement a fail-to-safe principle, an equivalent level of safety shall be achieved by redundancy and/or diagnostics and fault alarm to relevant manned control room. o The probability of single defects / failures causing inadvertent trip actions shall be as low as reasonably practicable (e.g. provide fault tolerance by means of automatic diagnostic features and redundancy). o All barriers or parts thereof, shall be protected against or withstand environmental conditions that may compromise their safety functions, e.g. ice, snow, sand, water, etc. Survivability of the barrier/barrier element, i.e. its ability to function under relevant accident scenarios and loads. Equipment with a safety function, during and after the accident, should be located so that the possible impact from accidental loads is minimised. To develop the survivability requirements, the design loads that shall form the basis for design of facilities, systems and equipment need to be determined, ref. subclause . Barriers/safety systems may be dependent on safety critical tasks to function, through e.g. monitoring, activation or control. For relevant safety systems, performance requirements should also be defined for operational / organizational barrier elements, ref. subclause 5.4. Each clause of this document from clause and onwards describes generic design principles and requirements for the different safety systems and barriers. The installation specific performance requirements shall be developed based on this framework to manage the risk. It may be beneficial to group the various performance requirements into performance standards including a description of the role of the safety functions. Dependencies on and interfaces with other systems should also be described. A Safety Requirement Specification (SRS) is a documentation of requirements related to safety instrumented systems (SIS). The SRS documentation shall be developed during projects and shall provide the design basis for required SIS.ly, the SRS shall contain the relevant key information for use in specifying and operating the instrumented safety functions. However, the information required may be contained in other project documents referred to in the SRS, e.g. performance standards. Duplication of information should be avoided. The SRS shall contain three main types of requirements: NORSOK S-001:2018 1NORSOK © 2018 functional requirements such as capacities and response times, integrity requirements such as PFD and SIL, and, operating prerequisites and constraints. Further reference is given to IEC 61511 (Functional Safety Œ Safety Instrumented Systems for the process industry sectorﬂ) and Norwegian Oil and Gas Association GL070.. that needs to be developed to deepen or clarify performance requirements when necessary. Ref. subclause . Also, see Annex C for proposed format and information for data sheets for selected Safety Equipment. 5.3 Risk reduction principles and inherent safety design In concept development, priority shall be given to solutions that are inherently safe. If the hazard cannot be eliminated, probability reducing measures should be given priority over consequence reducing measures. The objectives of risk reduction principles and inherent safety design are to: eliminate or reduce potential hazards/increase inherent safety by; reduction, e.g. reducing the hazardous inventories or the frequency or duration of exposure; substitution, e.g. substituting hazardous materials with less hazardous ones; attenuation (moderation), e.g. using the hazardous materials or processes in a way that limits their hazard potential; simplifications, e.g. making the facility and process simpler to design, build and operate, hence less prone to equipment, control and human failure; reduce probability of hazardous events; establish mitigating measures, e.g. through safety barriers. The ALARP principle (As Low As Reasonable Practicable) shall be used to select the safety solutions. 5.Design provisions for the operating phase Effective management of technical barriers in project development and design processes also need to address relevant dependencies with operational and organizational aspects for the operating phase. Some examples of interfaces between technical, operational and organizational aspects to be considered are: operational prerequisites for start-up and use; measures and restrictions that are necessary in the event of overriding, disconnection or in the event of missing/impaired safety systems and barriers; maintenance; competence; emergency preparedness; manual intervention. In order to ensure solutions which are suited for varying conditions, particular prerequisites shall be accommodated for in the design phase (and sustained during the operating phase). Examples of aspects that should be addressed are: assumptions including conditions and possible actions, when operating in different modes, i.e. normal, test, fault, failure, degraded. (Relevant assumptions in risk analyses should be according to requirements in the different installation specific performance standards); NORSOK S-001:2018 NORSOK © 2018 15 provisions, routines and logs for isolation of safety related functions during testing and maintenance, e.g. by inhibit (disabling input signal) and override (disabling output action). Such isolation should not render unnecessarily large parts of the system inactive. Logging, manual or automatic, of any such isolation action, e.g. time, number and duration, is mandatory; requirements for compensatory measures. (Responsible personnel for the operating phase will need to implement the necessary measures to remedy or compensate for non-conformities, missing or impaired barriers). The basis for inspection, testing and maintenance shall be described as part of project development in close liaison with the end user and be finalized before start-up. Important elements are: Systems, equipment and barriers shall be classified as regards the health, safety and environment consequences of potential functional failures. Information in performance standards shall regardless of other criticality analyses (e.g. according to NORSOK Z-008) be used as basis for categorizing safety critical equipment. An inspection-, testing- and maintenance programme for safety barriers shall be developed as part of project development. The programme should include test/inspection/maintenance methods and intervals. These shall be determined based upon regulatory requirements, company requirements, performance requirements, results/assumptions from analyses (e.g. SIL), criticality analysis (ref NORSOK Z-008), manufacturers™ recommendations, operating experience and relevant plant maintenance strategy. For i
128 | 6.4.6 Lifting and lay down
129
130
131
132 | 6.4.7 Storage and handling of explosives
133 | Explosives shall be stored and handled such that the risk of fire, explosion and falling/flying objects is as low as possible, e.g.: Area of storage shall have a low probability of impact from falling loads and heat radiation from possible fires threatening the storage area. Fire water shall be available for cooling of perforating guns in the event of fire in the area. See subclause 21.4.10.221.4.7 for requirements for fire water. The storage area shall be clearly marked and with restricted access. Quantities of stored explosive substances shall at any time be kept to a minimum. The duration of explosive substances storage at site shall be adapted to the planned period of use. Provisions should be in place to safely handle explosives that can constitute a risk in the event of a hazard and accident situation: o provisions for safe removal or relocation of explosives by cranes in the event of a fire in areas near the explosives should be available; o loaded perforating guns should be stored with end caps permitting pressure relief (venting) in the event of exposure to a fire. Explosives shall be secured so that they do not inadvertently explode during storage and use, e.g., electrically triggered perforation equipment shall be shielded against radio waves and other electrical fields. Detonators or initiators that require the enforcement of radio silence shall not be used.
134 | 6.4.8 Floating installations
135
136
137
138 | 6.4.9 Turret
139 | The turret arrangement design shall aim at achieving open naturally ventilated areas and minimising explosion pressure. Enclosed mechanically ventilated areas should be restricted to LER/LIR with control or special equipment that requires special protection or cannot be located in outdoor environment. Such enclosed premises shall have overpressure ventilation, with air taken from and exhausted to a non-hazardous area. Location of the premises themselves as well as their ventilation inlets shall take into account the prevailing wind directions. Where anchor winches are arranged on the deck below riser termination and ESD valves, the deck separating the areas shall be solid and gas tight. Turret areas and piping shall be designed to minimise the risk of jet fires towards tank tops.
140 | 6.4.10 Explosion design principles
141
142
143
144 | 6.4.11 Hot air exposure of helicopter deck
145 | Offshore installations will contain a variety of systems and processes that can emit gases and hot air plumes, typically generated by turbine generators, diesel engines, flares, and emergency depressurisation systems. Hot air flow from these systems may create turbulence and other thermal effects that may severely affect helicopter operations, unless adequate risk reducing measures are taken at the design stage. The design shall be in accordance with clause 5, NORSOK C-00Helicopter Deck on Offshore Installations. NORSOK S-001:2018 NORSOK © 2018 27 6.5
146 | 6.5 Survivability requirements
147
148
149
150 | 7 Structural integrity
151
152
153
154 | 7.1 Role
155
156
157
158 | 7.2 Interfaces
159
160
161
162 | 7.3 Required utilities
163
164
165
166 | 7.4 Functional requirements
167
168
169
170 | 7.5 Survivability requirements
171
172
173
174 | 8 Containment
175
176
177
178 | 8.1 Role
179
180
181
182 | 8.2 Interfaces
183
184
185
186 | 8.3 Required utilities
187
188
189
190 | 8.4 Functional requirements
191
192
193
194 | 8.4.1 General
195
196
197
198 | 8.4.2 Piping
199
200
201
202 | 8.4.3 Flanges and connections
203 | The number of mechanical connections (flanges and hubs) in systems with hydrocarbon inventory shall be kept to a minimum, i.e. by use of welded connections where feasible. Mechanical connections in a hydrocarbon piping system shall as a minimum conform to NORSOK L-001. NOTE It should be noted that flanges of a compact type, according to NORSOK L-005, have a significantly lower leak frequency as compared to traditional ASME flanges. Hence, a reduced risk level can be obtained by selecting compact type flanges. Relief/emergency depressurisation headers should be designed without flanges. Flanges for future tie-ins is acceptable. These shall be of a compact type. Passive fire protection shall be applied in accordance with subclause 20.4.3. NORSOK S-001:201NORSOK © 20129 There should be no flanges in hydrocarbon piping to, or through, the utility area to avoid hazardous classification and resulting requirements for additional safety systems and barriers. One flanged connection may be installed on the fuel line to each combustion engine, turbine and fired unit in the utility area as well as transfer lines in offloading systems in utility areas for connecting the equipment without affecting the area classification. With respect to instrument connections (connected to a piping valve) to hydrocarbon vessels, piping or equipment, the bore/orifice through the vessel-/piping wall (through nozzle) should be as small as possible to minimise the leak rate in the event of instrument connection leaks. Consideration shall be made to possible hydrate formation, wax deposit or plugging due to other deposits. A flanging philosophy should be established by relevant disciplines, taking into account the installation and operational risk of type of connections and welded solutions.ly, the number of flanges should be minimized.
204 | 8.4.4 Risers
205
206
207
208 | 8.5 Survivability requirements
209
210
211
212 | 9 Open drain
213
214
215
216 | 9.1 Role
217
218
219
220 | 9.2 Interfaces
221
222
223
224 | 9.3 Required utilities
225
226
227
228 | 9.4 Functional requirements
229
230
231
232 | 9.4.1 Minimize fire/escalation risk arising from spills and leaks
233 | Measures shall be provided for dealing with spills and leaks in all areas that have a source of flammable or hazardous liquid so as to minimize the risk of fires and personnel exposure to hazardous materials. The drainage systems shall be designed in accordance with NORSOK P-002 and ISO 13702. The capacity of the drainage system, i.e. including overflow lines for fire water, shall be able to handle full fire water capacity and the liquid leak rate associated with the worst credible process fire, typically 5 kg/s within the bunded area. The drain header capacity shall be sufficient to avoid backpressures that cause liquid to flow back into other open parts of the system during deluge/firefighting. Simultaneous deluge/firefighting in relevant number of areas shall be considered, according to the safety strategy. All tanks and vessels containing flammable liquids shall have a deck bunding covering the tank perimeter controlling spreading of spills, and there shall be drainage within the bunding. Design of the drain system to handle fire water on a floater is challenging due to vessel motions which may result in liquid flowing directly to sea. Particular attention should be made to prevent spreading of fire water and drainage between fire areas, decks and lower escape ways. Tanks collecting drains from hazardous areas shall be purged with inert gas to prevent explosive mixtures.
234 | 9.4.2 Separation of drain systems
235
236
237
238 | 9.5 Survivability requirements
239
240
241
242 | 10 Process safety system
243
244
245
246 | 10.1 Role
247
248
249
250 | 10.2 Interfaces
251
252
253
254 | 10.3 Required utilities
255
256
257
258 | 10.4 Functional requirements
259
260
261
262 | 10.4.1 Process safety principles
263 | The process safety functions shall provide a reliable and fast detection of process upsets and execution of the actions that are considered necessary to control the situation and avoid escalation. For topside functions, the PSD system shall be independent from the process control system. For subsea systems requiring PSD protection, the PSD function shall be independent of the subsea control system, i.e. if any failure of the subsea control system will require PSD protection, e.g overpressure protection. Process and auxiliary systems shall be designed such that no single failure during operations can lead to unacceptable hazardous situations. The process safety system shall normally provide two levels of protection to prevent or minimize the consequences of an undesirable event within the process. If practicable, the two levels shall be provided by functionally different types of device. The design shall be in accordance with NORSOK P-002. Process safety layers of protection shall be established and designed in accordance with API RP 14C or ISO 1041including referenced process standards that in a prescriptive manner often make recommendations of conventional solutions. Note that ISO 1041in subclause 6.2.15 states that if an instrument-based system is used for primary protection, it will not need to comply with IEC 61511-1 provided the secondary protection system is self-actuating (PSV or rupture disc) and meets the requirements of relevant codes and standards. Then, a deterministic approach based upon industry accepted typical protective solutions is also acceptable for PSD functions, e.g predefined performance requirement (PFD values) as established in Norwegian Oil and Gas Association GL070. In order to avoid cascading effect, the process shutdown shall be realized in accordance with ISO 10418, 6.2.1/ API RP 14C, 4.2.3. Where utilities, such as cooling water, are shared by process systems and equipment in non-hazardous areas, the utility system shall be designed to prevent migration of flammable liquids and gases into non-hazardous areas and systems. Loss of instrument air or hydraulic supply (PALL) shall initiate a full production shutdown.
264 | 10.4.2 Process shutdown (PSD) valves
265
266
267
268 | 10.4.3 Pressure safety valves (PSVs)
269
270
271
272 | 10.4.4 Alarms, automatic actions
273 | Alarms shall support operator decision-making during upsets and accidental situations. Actions shall be initiated automatically when process or equipment protection limits are exceeded.
274 | 10.4.5 Response time
275
276
277
278 | 10.4.6 Logic solver
279 | The logic solver (firmware, as standard manufacturer provision) shall be in compliance with IEC 61508/IEC 61511 and Norwegian Oil and Gas Association GL070.
280 | 10.4.7 Instrument based systems for secondary pressure protection
281
282
283
284 | 10.5 Survivability requirements
285
286
287
288 | 11 Emergency shutdown (ESD)
289
290
291
292 | 11.1 Role
293
294
295
296 | 11.2 Interfaces
297
298
299
300 | 11.3 Required utilities
301
302
303
304 | 11.4 Functional requirements
305
306
307
308 | 11.4.1 Manual ESD activation
309 | Manual activation of the ESD system shall be possible from strategically positioned stations where accessibility and manning in a hazard situation is taken into account. Possibility for manual activation should be provided at strategic positions such as: CCR (APS/ESD1/ESD2); helideck (APS); muster areas/lifeboat stations (APS); bridge connections (ESD2); NORSOK S-001:2013NORSOK © 201drilling areas (driller shutdown and ESD2); exits from process and wellhead areas (ESD2); strategic located stations along escape routes (ESD2). APS activation possibility to be considered at bridge landings in addition to CCR. Manual activation buttons shall be protected against inadvertent activation, e.g. with protective covers or rotary switch and duplicated buttons for APS. Each activation button shall be clearly marked, and a consistent colour coding shall be applied for the activation buttons, e.g. black with yellow stripes for APS and yellow for ESD2. Isolation of emergency power supplies i.e. UPS upon APS shall be executed via a timer independent of the logic solver, normally 30 min to ensure that necessary safety critical equipment is in operation during escape and evacuation. Separate function(s) shall be provided allowing bypassing timer based APS countdown. An independent function, e.g. disconnecting the power to the ESD logic solvers, shall be included allowing safe shutdown upon failure of programmable logic. The function may be realized by setting the installation in a safe state, i.e. initiating emergency depressurization and shutdown equivalent to an ESD1 level. Special consideration shall be made to disconnection of centralised escape lights such that no single fault shall result in disconnection of all escape lights.
310 | 11.4.2 Emergency shutdown (ESD) final elements
311
312
313
314 | 11.4.3 Emergency shutdown (ESD) actions
315 | The ESD system shall activate all actions in accordance with the Safety Strategy. Consideration shall be given to interrelations between interconnected installations, e.g. by pipelines or control systems. The ESD functions shall be arranged in a tree-structured hierarchy, APS, ESD1 and ESD2. principles are shown in Figure and should be used as basis for the facility specific safety strategy. The ESD hierarchy should be simple and unambiguous minimizing number of sub-levels. A higher ESD level shall initiate lower levels including PSD. A signal on a certain level should never initiate shutdowns or actions on higher levels. ESD actions shall include depending on ESD level (see Figure 4): shutdown of dry well trees, riser valves and subsea well trees when wells are located within the platform safety zone. NOTE with reference to Figure 4, shutdown will include closure of DHSV and/or SSIV for specific scenarios; initiate stop of subsea pipeline and flowlines connected to the installation outside of the platform safety zone. The closure signal for both subsea wells and other imports can be realized in subsea control system, except upon APS and F&G detection in riser area where isolation is performed by ESD power cut to subsea facility, ref 11.4.5. For other imports, the ESD system submits a PSD signal (or by fail to safe PCS signal) to the connected sources (riser valves), ref. subclause 10.4.1; shutdown and sectioning of the hydrocarbon process facilities; initiation of EDP; ignition source isolation; shutdown of main power generation; start/stop of emergency power generator via voltage sensor; shutdown of drilling, intervention and work-over equipment not required for well control. Any shutdown, spurious or intended, shall require a manual reset from CCR. During well intervention DHSV and master valves shall be disconnected from the platform ESD system. It shall be possible to operate the DHSV and master valves in accordance with subclause 26.5. NORSOK S-001:2013NORSOK © 201Loss of ESD signals between an NNMI and remote control centre shall shutdown the NNMI upon a time delay. The time delay should not exceed 10 min. ESD of the remote control centre shall result in shutdown of the NNMI. When installed, remotely operated Subsea Isolation Valves (SSIV) shall as a minimum be automatically closed upon APS activation and confirmed fire or gas detection in riser area. The X-mas tree valves part of the ESD function of well stream isolation shall, for subsea installations, apply a fail-to-safe principle for both electrical and hydraulic power supplies. Figure Š Emergency shutdown (ESD) (principal hierarchy Œ more detailed and other requirements apply) Notes (a) The closure signal for both subsea and other imports can be realized in PCS, except upon F&G detection in riser area where isolation is performed by ESD (power cut to subsea facility, ref 11.4.5) or PSD (other imports). (b) Alternative to ESD1 can be ESD2 and selective electrical isolation disconnection depending on location, e.g. located in close proximity to process, wellhead or drilling areas. (c) Dampers closed/fans stopped on single gas alarm in ventilation intake. (d) The start function shall be inhibited if gas has been detected in air intakes to generator, or generator has previously been tripped due to overspeed. Inhibit start of emergency generator may be also considered due to ISC. For power supplied from subsea cable, the emergency generator only to start upon loss of all cable supplied power. (e) Activation of firefighting systems manually via deluge release pushbutton (not via pressure transmitter feedback, see subclause 21.4.4) shall only initiate ESD2 and not automatic depressurization. Automatic NORSOK S-001:201NORSOK © 20139 EDP at confirmed gas detection shall be evaluated as a mean to limit extent and duration of possible gas leaks, ref subclause 12.4.2. (f) Annunciation (alarm and personnel warning) shall be given together with relevant shutdown level. (g) Immediate shutdown of equipment can be required, see subclause 15.4.4. (h) Shutdown of main generator will also include essential generator, if installed (trip both production and drilling). Main power generation until ESD1 premises dual fuel generators. (i) Activation of DHSV and ASV on detection in wellhead area refers to topside wells. Refer to key (a) for subsea wells. (j) Main power switchboard if power is supplied from subsea cable. Emergency board should be operative as long as possible to avoid need for start-up of emergency generator, ref. key (d). (k) For typical emergency consumers in drilling mode, refer to clause 15 and NORSOK D-001. (l) On confirmed gas unless otherwise specified in Safety Strategy (see Clause 13, Table 2). (m) With respect to possible ignition sources (Ex equipment), see subclauses 15.4.1, 15.4.2 and 15.4.3. (n) The intention of the LAHH on ESD2 level is to provide a secondary instrumented process protection level. As an alternative to initiation of ESD2, shutdown of relevant ESD valves (using the ESD solenoid valves) and initiation of PSD is acceptable. PSD does not initiate general alarm, stop of fuel gas and ignition source isolation.
316 | 11.4.4 Emergency shutdown (ESD) alarm annunciation
317
318
319
320 | 11.4.5 Emergency shutdown (ESD) response time
321
322
323
324 | 11.4.6 Logic solver
325
326
327
328 | 11.4.7 Emergency shutdown (ESD) independence
329
330
331