## Sheet1
| Chapter | Result
0 | Introduction | []
1 | 1 Scope | []
2 | 2 Normative references | [' Latest issue of the references shall be used unless otherwise agreed']
3 | 3 Terms and definitions | ['shall (requirement)\nexpression in the content of a document conveying objectively verifiable criteria to be fulfilled and from which no deviation is permitted if compliance with the document is to be claimed\n\nNote 1 to entry:\tRequirements are expressed using the verbal forms specified in ISO/IEC Directives, Part 2 clause 7']
4 | 5 Management of technical safety | []
5 | 5.1 General | [' studies, analysis and design reviews) shall be provided with due consideration for timely input to design and procurement processes', '\n\nA follow-up system shall be established that enables proper documentation, handling, follow-up and closeout of agreed actions and recommendations from the various studies and analyses in the project', '\n\nIn the event space is allocated for future expansions in new project developments, the design should incorporate sufficient flexibility to include capacity for the additional equipment, e']
6 | 5.2 Activities related to technical safety design | []
7 | 5.2.1 Overview | []
8 | 5.2.2 Define Context | []
9 | 5.2.3 Identify hazards and accidental events (HAZID) | ['\n\nBased on hazard identifications it shall be possible to present an overview of possible hazards and accidental events that can occur in different areas and during different activities', ' The structure of HAZIDs should preferably be area based, but for some cases they may also be a HAZID node (e']
10 | 5.2.4 Perform risk analyses and evaluations | ['Risk and safety analyses / studies shall be performed to establish sufficiently detailed information about the risk associated with the identified hazards and accidental events']
11 | 5.2.5 Identify and define barrier functions, systems and elements (risk treatment) | ['The need for barrier functions shall be established based on the context, identified hazards and accidental events, risk analyses and risk evaluation activities', ' Documentation shall be prepared so that it is possible to identify the need for barrier functions in each installation area or relevant HAZID node', '\n\nWhen the need for barrier functions are identified, systems and elements necessary for realizing the barrier functions shall be defined', ' Therefore, operational and emergency situation considerations shall be an integral part of technical barrier process', ' As part of project development, safety system design shall include a human factors study amongst others documenting the following:\n\n- Identification of safety critical tasks (“operational barrier elements”) required for the safety system to function', ' These include who is responsible for performing a task, under what circumstances it is expected to be performed, available response time and how it shall be carried out', '\n\nThe results from the study shall be used as input to design, as well as preparations for operations', ' Input to design should include HMI and alarm system specifications, levels of automation, equipment labelling, system capacities and tolerances']
12 | 5.2.6 Safety strategies | ['Documentation shall be prepared to record how specific hazards or accidental events are managed by the use of barrier functions, systems and elements', '\n\nSafety strategy documentation should also be prepared to outline applicable overall principles for design, layout, arrangement, philosophies and other high-level design and operational aspects related to barriers; e']
13 | 5.2.7 Define performance requirements | ['Verifiable performance requirements shall be established to ensure that the barrier function is fulfilled', ' Performance requirements shall be established as an integrated part of the design and construction process, as the decisions on what safety systems and barriers to install and their corresponding specifications are made', ' The following general requirements apply:\n-Design and realisation, inclusive of relevant operating issues, of all safety instrumented systems (SIS) shall be based upon the principles of IEC 61508/IEC 61511', '\n-The applicable safety system, or affected parts of it, shall be designed to fail-to-safe principle, whereby the system goes to a predefined safe state in the event of detectable malfunction', ' It shall be designed with the aim of avoiding single defects / failures that may prohibit safety actions being executed', ' If it is not feasible to implement a fail-to-safe principle, an equivalent level of safety shall be achieved by redundancy and/or diagnostics and fault alarm to relevant manned control room', '\n-The probability of single defects / failures causing inadvertent trip actions shall be as low as reasonably practicable (e', '\n-All barriers or parts thereof, shall be protected against or withstand environmental conditions that may compromise their safety functions, e', ' To develop the survivability requirements, the design loads that shall form the basis for design of facilities, systems and equipment need to be determined, ref', ' The installation specific performance requirements shall be developed based on this framework to manage the risk', ' Equipment with a safety function, during and after the accident, should be located so that the possible impact from accidental loads is minimised', ' For relevant safety systems, performance requirements should also be defined for operational / organizational barrier elements, ref']
14 | 5.2.8 Define performance Standards | [' Dependencies on and interfaces with other systems should also be described']
15 | 5.2.9 Establish safety requirement specifications (SRS) | [' The SRS documentation shall be developed during projects and shall provide the design basis for required SIS', '\n\nGenerally, the SRS shall contain the relevant key information for use in specifying and operating the instrumented safety functions', '\n\nThe SRS shall contain three main types of requirements:\n \n\n\n- functional requirements such as capacities and response times,\n-integrity requirements such as PFD and SIL, and,\n-operating prerequisites and constraints', ' Duplication of information should be avoided']
16 | 5.2.10 Safety specifications, diagrams, drawings, philosophies, etc. | []
17 | 5.3 Risk reduction principles and inheret safety design | ['In concept development, priority shall be given to solutions that are inherently safe', '\n\nThe ALARP principle (As Low As Reasonable Practicable) shall be used to select the safety solutions', ' If the hazard cannot be eliminated, probability reducing measures should be given priority over consequence reducing measures']
18 | 5.4 Design provisions for the operating phase | ['\n\nIn order to ensure solutions which are suited for varying conditions, particular prerequisites shall be accommodated for in the design phase (and sustained during the operating phase)', '\n\nThe basis for inspection, testing and maintenance shall be described as part of project development in close liaison with the end user and be finalized before start-up', ' Important elements are:\n\n-Systems, equipment and barriers shall be classified as regards the health, safety and environment consequences of potential functional failures', ' Information in performance standards shall regardless of other criticality analyses (e', '\n-An inspection-, testing- and maintenance programme for safety barriers shall be developed as part of project development', ' These shall be determined based upon regulatory requirements, company requirements, performance requirements, results/assumptions from analyses (e', '\n-Systems shall be established for monitoring barrier integrity, including possible deficiencies and degradation', ' Examples of aspects that should be addressed are:\n\n-assumptions including conditions and possible actions, when operating in different modes, i', ' (Relevant assumptions in risk analyses should be according to requirements in the different installation specific performance standards);\n \n\n\n-provisions, routines and logs for isolation of safety related functions during testing and maintenance, e', ' Such isolation should not render unnecessarily large parts of the system inactive', ' The programme should include test/inspection/maintenance methods and intervals', '\n-The safety functions/systems should, where reasonably practicable, allow for the required testing to be carried out without interrupting production or operations', ' The system should be established and populated with data during commissioning']
19 | 5.5 Commissioning and start-up | ['Safety management during installation, start-up and the operating phases shall be defined in specific commissioning and operating procedures', ' The commissioning test shall be performed under as realistic operating conditions as possible', '\n\nThe fire water system shall be subject to full scale dimensioning fire water demand scenario test, i', '\n\nRelevant experience from commissioning and start-up shall be transferred to the operational phase', '\n\nSafety related systems/functions required for safe project execution shall be operational to reflect the risk when the facility is gradually moved from construction to full operational status', ' Systems required for life support, communication, evacuation, fire detection, active and passive fire protection shall be operational when the facility is to be inhabited']
20 | 5.6 Accidental loads and resistance | []
21 | 5.6.1 General | ['The accidental loads/actions that can affect facilities or parts of facilities shall be determined', ' Also, the design loads that shall form basis for design and operation of facilities, systems and equipment need to be determined', ' Determination of design loads shall ensure that both deterministic and functional requirements in applicable regulations are met', ' The chosen design accidental loads that are to be used as basis for design shall ensure that facilities, systems and equipment are designed in such a way that relevant accidental situations will not result in unacceptable consequences', '\n\nIn addition to loads described in the subsequent sections, the following loads shall be included (ref']
22 | 5.6.2 Gas explosions | ['\n\nDesign explosion loads shall be established using a recognised method (e', '\nExplosion loads shall be defined for relevant horizontal and vertical area dividers (pressure and impulse from explosion) and relevant equipment (pressure/drag forces)', ' Explosion loads shall also be defined for areas external to the initial explosion location (typical LQ, utility modules etc', ' An explosion study should be performed at an early stage, enabling the key installation parts to be located favorably with regard to explosion', '\n\nEquipment that can become a flying object and can significantly impair critical safety equipment/structures such as fire divisions, riser valves, wellheads, blowdown piping, should be considered secured']
23 | 5.6.3 Hydrocarbon fire | []
24 | 5.6.3.1 General | []
25 | 5.6.3.2 Main load bearing structure | [' A validated computational fluid dynamics (CFD) model shall be used to provide realistic modelling of the fire source and the effect of the surroundings in order to define the design accidental load', ' Care shall be taken when selecting simulation cases', ' Either these shall be selected and used conservatively, or a larger number of simulations are necessary to be statistically representative']
26 | 5.6.3.3 Worst credible process fire | ['\n\nThe load from the WCPF shall be covered by the design accidental load for main load bearing structures and fire divisions', ' The identified WCPF shall not escalate to hydrocarbon pipeline risers or to wells (flow from reservoir) to avoid impairment of the main load bearing structures', ' For wellhead areas, gas lift volumes in well annuli shall be included in the evaluation to determine the WCPF, unless the supply to the annulus is protected with a hydraulically activated integrated wellhead valve, i', '\n\nWhen assessing the WCPF, consequences of possible escalation to one other ESD segment (including the largest gas lift annulus volume unless protected as described above), shall be taken into account']
27 | 5.6.3.4 Unacceptable ruptures of process equipment in a fire situation | [' These values shall be carefully considered for the actual use (i', ' If any emergency action can lead to the presence of personnel close to the fire, this shall be taken into account', ' personnel in the far end or personnel involved in well securing (closure of well valves and/or BOP) during well interventions shall be accommodated for', '\n\uf0be\tPipes\no\tInstantaneous release shall not prevent all escape possibilities for personnel anywhere on the installation to reach Muster Areas', '\no\tHydrocarbon release rate from any one escalation caused by a small jet fire (250 kW/m2) shall not exceed 2 kg/s until personnel have escaped the area of the fire', ' For areas difficult to get out of, this time shall be prolonged', '\no\tHydrocarbon release rate from any one escalation caused by fires larger than 2 kg/s, shall not exceed the initial fire size until personnel have escaped the area of the fire', '\no\tFor the first two minutes after escape from the area of the fire, gas release rate from any escalation shall not exceed 10 kg/s to accommodate safe escape from all other areas (this rate will normally not impair all escape routes from other areas)', '\n \n\n\no\tHydrocarbon release rate from any escalation shall not exceed 100 kg/s (typical value to avoid excessive heat radiation and smoke impairment) until all personnel have reached the Muster Areas', '\no\tIn early screening work, larger fires can be represented with 350 kW/m2 and should not escalate with more than 5 kg/s']
28 | 5.6.3.5 Process equipment and piping – fire calculations | ['\n\nWhen calculating if and when process segments will rupture due to jet fire exposure due to material weakening, the heat exposure from a leak should be evaluated by assessing two representative points in the fire as follows:\n\n\uf0be\tPoint 1: Using the maximum duration of a leak rate from any ESD segment in the area above 2 kg/s as the duration with local peak heat load of 350 kW/m2 (representing a point at some distances from the leak)']
29 | 5.7 Qualification of technology | [' The technology shall be qualified following a systematic approach, such as laid down in DNV-RP-A203 [1] or similar guideline, in order to demonstrate that it meets specified functional requirements and reliability targets']
30 | 5.8 Experience transfer | ['To ensure transfer of technical safety experience from relevant installations in operation, experience transfer activities should be part of the project development process', ' Sources of experience should include\n\n-operational experience of relevant installations,\n-project execution of relevant installations and modification to these,\n-good technical solutions,\n-solutions/equipment to be avoided']
31 | 5.9 Temporary equipment | ['Temporary equipment shall be in accordance with NORSOK Z-015 Temporary Equipment and follow the relevant principles of this document, e', ' For temporary equipment operated as self-contained units, well completion and workover units etc, the interfaces shall be considered in the design phase both for normal and emergency situations, e', ' Main lay-down areas should be prepared for connection of containers and temporary equipment to the platform’s Fire & Gas system']
32 | 5.10 Documentation | ['\n\nSafety interface documentation shall be produced where relevant in order to ensure that safety requirements are addressed and implemented in the development of the design and between different contractors and installations, e', 'The following safety documents should be developed during development of a new installation and be kept updated during the lifetime of the installation:\n\n\uf0be\tRisk assessments (HAZID, HAZOP, risk analysis, risk evaluations, etc']
33 | 6 Layout | []
34 | 6.1 Role | ['The layout and arrangement of an installation shall reduce probability and the consequences of accidents through location, separation and orientation of areas, equipment and functions']
35 | 6.2 Interfaces | []
36 | 6.3 Required utilities | []
37 | 6.4 Functional requirements | []
38 | 6.4.1 Main design principles | ['The installation(s) shall be oriented with respect to the dominant wind direction to minimize the likelihood of a gas release or smoke drifting towards the accommodation and primary evacuation means', '\n\nThe installation shall be divided into main areas (accommodation, utility, drilling, wellhead, process and hydrocarbon storage)', ' The main areas shall be located and designed to minimize the risk to people, environment and assets', ' Main areas shall normally be separated by use of physical barriers as fire and blast divisions to prevent the escalation of an accident from one main area to another', ' blowouts and riser fires on the neighbouring installations shall be assessed', '\n\nMuster areas, accommodation, evacuation means and escape routes shall be located where they are least affected by fires and explosions', '\n\nSafety systems shall be located or protected to ensure operation during relevant emergency conditions', ' Systems and equipment such as FW pump units, emergency generator(s) and switchboards, UPS, ESD/ F&G nodes, ballast and position keeping controls shall be located as safe as possible in the accommodation or utility area', '\n\nCCR shall be located as safe as possible in the accommodation or utility area with easy and safe access to evacuation facilities', '\n\nEquipment and piping containing hydrocarbons shall be located or protected to minimize consequences from dropped objects, crane boom fall and swinging loads etc', '\n\nVentilation inlets, including combustion air inlets, shall be located in a safe area with respect to accidental gas leakages, ref', ' Doors bordering naturally ventilated areas shall be self-closing and conform to fire partition requirements', ' for noise suppression, shall be subject to special consideration with respect to required safety functions', ' The utility area should serve as a barrier between hazardous areas and LQ', ' The PSD node should be located in the same room as the ESD/F&G nodes, reference is made to subclause 10', '\n\nDoors from non-hazardous rooms facing directly towards hazardous areas should be avoided', ' Non- hazardous rooms with doors or openings less than 3 m away from hazardous area should be avoided', ' Such consideration should include impacts to F&G detection, fire water, drain, ventilation (effect on explosion overpressure and source of ventilation - see 17', ' The equipment enclosures should be made as small as possible in order to avoid it becoming a separate detection/fire area']
39 | 6.4.2 Riser flow line area | ['Hydrocarbon risers and associated equipment shall be designed and located to minimise risk due to accidental events (such as gas leakages, fires, explosions, ship impact and dropped objects), including accidents where riser or associated equipment is the initial source', '\n\nPig launchers and receivers shall be located in open naturally ventilated areas at the periphery of the platform facing sea, and with hatches directed away from equipment and structures', ' It shall not be possible to open pressurized pig launchers/receivers', '\n \n\n\nRisers and riser ESD valves shall be located or protected to minimize the likelihood of damage below the ESD valves causing release of pipeline/riser inventories', ' The riser shall be protected against design accidental loads', '\n\nThe riser ESD valves shall be located as close to sea-level as practicable, i', ' Riser ESD valves should be located in open, naturally ventilated area and such that liquid accumulation below the valve is avoided']
40 | 6.4.3 Process area | ['Fire and explosion assessments shall be performed along with the development of the layout to minimise the built-in escalation potential', ' This shall be ensured through the following principles:\n\n-Equipment and piping containing high-pressure gas should be located in the upper decks above the module support frame or main hull', '\n\nProcess vessels, process piping, pig launchers and receivers and other hydrocarbon containing equipment shall be protected from external impact (e', ' This shall be ensured through the following principles:\n\n-Equipment and piping containing high-pressure gas should be located in the upper decks above the module support frame or main hull', '\n-Liquid vessels should be located lower than gas equipment', '\n-low-pressure equipment containing large amount of liquids should be located and arranged so that exposure to jet fires is minimised']
41 | 6.4.4 Well areas | ['Drilling risers and conductors shall be designed and positioned or protected to minimize the likelihood of damage, including that due to ship impact and dropped objects', '\n\nFor installations with main support frame (MSF), the wellheads should be located above the MSF in order to reduce exposure of the MSF from a wellhead fire']
42 | 6.4.5 Piping | ['Routing of piping containing hydrocarbon to or through the utility area shall be avoided except for fuel lines to utility systems', ' Hydrocarbon piping shall not be routed within the LQ areas', '\n\nTo avoid area classification of production laboratory, pressure control valves for flammable gases shall be located in open air outside laboratory', '\n\nRouting of hydrocarbon piping within areas where emergency equipment is located shall be limited to diesel fuel supply lines for emergency equipment themselves', '\n\nHydrocarbon transfer lines to/from bridges should be routed as safe as possible, preferably along the periphery of the installation', '\n\nPipework containing flammable liquid should not be routed such that a leak can come into contact with hot surfaces with temperature exceeding auto-ignition temperature, e']
43 | 6.4.6 Lifting and lay down | ['Crane coverage and lay down areas shall be arranged to promote safe crane operations with free visibility from crane cabin and minimise the risk of dropped objects', ' Considerations shall be given to sidewise movement of load', '\n\nWithin defined lifting zones equipment, or piping, containing hydrocarbons, flammable or toxic gas/liquid shall be protected from dropped objects', '\n\nLifting above high voltage equipment and cables shall be assessed, and protection shall be considered installed', '\n\nThe lifting zones shall be defined and shown on the lifting map in crane cabin', ' Allowable weight chart for laydown areas shall be established', ' Location of laydown areas and temporary storage of equipment shall be considered to minimize effect on explosion overpressure, ventilation, flying debris from explosions and possible negative effects on technical barriers (e', ' Crane software should give alarm in crane when lifting restriction boundaries are exceeded', '\n\nLaydown and storage area should not be located in hazardous area']
44 | 6.4.7 Storage and handling of explosives | ['Explosives shall be stored and handled such that the risk of fire, explosion and falling/flying objects is as low as possible, e', ':\n\n\uf0be\tArea of storage shall have a low probability of impact from falling loads and heat radiation from possible fires threatening the storage area', ' Fire water shall be available for cooling of perforating guns in the event of fire in the area', '\n-the storage area shall be clearly marked and with restricted access', '\n-Quantities of stored explosive substances shall at any time be kept to a minimum', ' The duration of explosive substances storage at site shall be adapted to the planned period of use', '\n-Explosives shall be secured so that they do not inadvertently explode during storage and use, e', ', electrically triggered perforation equipment shall be shielded against radio waves and other electrical fields', ' Detonators or initiators that require the enforcement of radio silence shall not be used', '\n-Provisions should be in place to safely handle explosives that can constitute a risk in the event of a hazard and accident situation:\n-provisions for safe removal or relocation of explosives by cranes in the event of a fire in areas near the explosives should be available;\n-loaded perforating guns should be stored with end caps permitting pressure relief (venting) in the event of exposure to a fire']
45 | 6.4.8 Floating installations | ['For floating installations, the following shall apply:\n\n\uf0be\tSystems with hydrocarbons with flashpoint below 60 °C shall not be installed in columns or pontoons for floating installations', ' maritime control/bridge, process control and special emergency preparedness functions) shall be arranged in one common control centre for the entire installation', '\nProcess area shall be separated from FPSO hydrocarbon storage tank top by air gap of minimum 3 m and plated deck and bunding in order to avoid hydrocarbons spreading to the storage tank deck', "\n-The effects of 'green sea' shall be carefully evaluated and means of protection arranged", '\n-Submerged crude pumps shall be used for FPSOs', ' If submerged pumps are not selected for FSUs, the decision shall be supported by a safety study', '\n-Crude oil transfer lines or any other hydrocarbon line shall not be located in double bottom', ' exhaust ducts and generators) should be located upwind of potential leak sources on floating installation that will be turned up against the wind']
46 | 6.4.9 Turret | ['The turret arrangement design shall aim at achieving open naturally ventilated areas and minimising explosion pressure', ' Such enclosed premises shall have overpressure ventilation, with air taken from and exhausted to a non- hazardous area', ' Location of the premises themselves as well as their ventilation inlets shall take into account the prevailing wind directions', '\n\nWhere anchor winches are arranged on the deck below riser termination and ESD valves, the deck separating the areas shall be solid and gas tight', '\n\nTurret areas and piping shall be designed to minimise the risk of jet fires towards tank tops', ' Enclosed mechanically ventilated areas should be restricted to LER/LIR with control or special equipment that requires special protection or cannot be located in outdoor environment']
47 | 6.4.10 Explosion design principles | ['The amount of explosion relief available, the degree of blockage and congestion in an area of an explosion shall be optimised to reduce explosion risk', '\n\nThe use of explosion panels and weather protection shields shall be kept to a minimum', ' Natural ventilation and open modules shall be preferred', ' Cable trays, junction boxes, piping and equipment shall be located so that they will not significantly increase turbulence, block explosion ventilation openings and reduce the free vent area, and thus increase explosion loads', '11, should be followed', ' Where such arrangements are likely to cause an unacceptable working environment, special solutions such as temporary shields for maintenance operations should be considered']
48 | 6.4.11 Hot air exposure of helicopter deck | [' The design shall be in accordance with clause 5, NORSOK C-004 Helicopter Deck on Offshore Installations']
49 | 6.5 Survivability requirements | ['Equipment with a safety function, during and after the accident, shall generally be located and protected such that its role and function are maintained']
50 | 7 Structural integrity | []
51 | 7.1 Role | ['The structural integrity shall withstand all design load conditions (action) under normal operation and also ensure that the relevant safety functions are maintained after impact from design accidental loads ']
52 | 7.2 Interfaces | []
53 | 7.3 Required utilities | []
54 | 7.4 Functional requirements | ['Load bearing structures shall be designed with sufficient robustness in accordance with NORSOK N-001']
55 | 7.5 Survivability requirements | ['The design shall ensure sufficient structural integrity to withstand design accidental loads', ' The capacity of main load bearing structures shall as a minimum be maintained until the facility has been evacuated and be designed in accordance with requirements in NORSOK Z-013, NORSOK N-003 and NORSOK N-001', ' The design accidental fire load for the structure shall as a minimum include the worst credible process fire, ref', ' from well blowout) and consequences for neighbouring installations shall be considered (e']
56 | 8 Contrainment | []
57 | 8.1 Role | ['The containment function shall prevent release of hydrocarbons, other flammable fluids and/or harmful fluids (chemicals, toxic gases, steam, etc']
58 | 8.2 Interfaces | []
59 | 8.3 Required utilities | []
60 | 8.4.1 General | [') shall be designed, constructed, maintained and operated with the aim to avoid leaks to occur', '\n\nAll components and systems shall be designed to enable necessary inspection, testing and correction in compliance with established inspection and maintenance program']
61 | 8.4.2 Piping | ['The use of flexible hoses connected to processing systems shall be minimized, e', ' there should be a fixed system for annulus de-pressurization of gas lift wells', '\n\nThe use of flexible hose connections for well stream transfer within the turret and between turret and ship, should be minimised']
62 | 8.4.3 Flanges and connections | ['The number of mechanical connections (flanges and hubs) in systems with hydrocarbon inventory shall be kept to a minimum, i', ' Mechanical connections in a hydrocarbon piping system shall as a minimum conform to NORSOK L-001', ' These shall be of a compact type', ' Passive fire protection shall be applied in accordance with subclause 20', ' Consideration shall be made to possible hydrate formation, wax deposit or plugging due to other deposits', '\n\nNOTE\tIt should be noted that flanges of a compact type, according to NORSOK L-005, have a significantly lower leak frequency as compared to traditional ASME flanges', '\n\nRelief/emergency depressurisation headers should be designed without flanges', '\n \n\n\nThere should be no flanges in hydrocarbon piping to, or through, the utility area to avoid hazardous classification and resulting requirements for additional safety systems and barriers', '\n\nWith respect to instrument connections (connected to a piping valve) to hydrocarbon vessels, piping or equipment, the bore/orifice through the vessel-/piping wall (through nozzle) should be as small as possible to minimise the leak rate in the event of instrument connection leaks', '\n\nA flanging philosophy should be established by relevant disciplines, taking into account the installation and operational risk of type of connections and welded solutions', ' Generally, the number of flanges should be minimized']
63 | 8.4.4 Risers | ['The following applies above sea level for the riser side of the ESD valve for pipelines containing flammable fluids:\n\n\uf0be\tFlanges on the pipeline side of the riser ESD valves shall not be used for fixed steel type risers', ' The benefit of installing an SSIV shall be evaluated', '\n\uf0be\tFor flexible risers an SSIV shall be installed at the riser base', ' Mechanical connections shall be leak tested via a test port to verify leak tight assembly before the riser is filled with fluid for pressure and leak testing', ' The bolts and flanges shall have passive fire protection', '\n\nWith respect to flexible risers particular attention shall be made to the design, operation, condition monitoring and inspection to ensure pressure containment integrity during the whole lifetime of the risers', '\n\nFor both flexible risers and steel type risers, a tie-in connection is acceptable subsea if;\n\n\uf0be\tthe flexible pipe attached to the connector shall be specified in accordance with API Spec 17J, while the rigid pipe attached to the connector shall be specified in accordance with DNVGL-ST-F201;\n\uf0be\tthe location of the connector is optimised (distance, water depth) such that possible risk impacts are reduced as far as practicable;\n\uf0be\tdesign and performance verification of subsea flanges and hubs shall be according to ISO 10423;\n\uf0be\tfor a flanged connection, compact flanges according to NORSOK L-005 shall be used for flexible risers', ' In such cases two instrumented safety function shall be implemented ref', ' A PSV shall also be installed to cater for HIPPS\n \n\n\nleaks', ' If the PSV is required to meet the overpressure criteria in accordance with SIL allocation for the involved safety function, the relief and flare capacity shall be adjusted accordingly', '\n\nWith reference to Figure 3 the PSV arrangement shall comply with the following:\n\n\uf0be\tAn ESD valve upstream Riser PSV to be installed and located as close as possible to the offtake from the riser', '\n\uf0be\tThe ESD valve shall be welded, i', '\n\uf0be\tThe ESD valve shall receive automatic shutdown signal on confirmed fire detection in the riser area and location of Riser PSV as well as on APS', ' The flanges should be of compact type, see NORSOK L-005', ' The ESD valve should not receive any other automatic shutdown signals (from e', '\n\uf0be\tThe ESD valve should be fail in position and have fire/heat protection of valve, actuator and signal cable similar to the Riser ESD valve', ' The fire / heat protection should in addition to the riser valve fire integrity requirement, also ensure valve closure upon demand when exposed to jet fire\n(for ~4-5 minutes)', '\n\uf0be\tLocal reset function of the ESD valve as required for other ESD valves should not be implemented to ensure possibility of remote operation of the ESD valve from CCR', '\n\uf0be\tIt should be ensured that the riser is not the weakest point of the pipeline/riser system']
64 | 8.5 Survivability requirements | ['4), shall resist the design accidental loads they can be exposed to', ' To decide which hydrocarbon segments that shall withstand design fire load, see subclause\n5', ' With respect to explosion loads the design accidental load should be applied to the equipment and piping within the containment function']
65 | 9 Open drain | []
66 | 9.1 Role | []
67 | 9.2 Interfaces | []
68 | 9.3 Required utilities | []
69 | 9.4 Functional requirements | []
70 | 9.4.1 Minimize fire/escalation risk arising from spills and leaks | ['Measures shall be provided for dealing with spills and leaks in all areas that have a source of flammable or hazardous liquid so as to minimize the risk of fires and personnel exposure to hazardous materials', ' The drainage systems shall be designed in accordance with NORSOK P-002 and ISO 13702', ' including overflow lines for fire water, shall be able to handle full fire water capacity and the liquid leak rate associated with the worst credible process fire, typically 5 kg/s within the bunded area', ' The drain header capacity shall be sufficient to avoid backpressures that cause liquid to flow back into other open parts of the system during deluge/firefighting', ' Simultaneous deluge/firefighting in relevant number of areas shall be considered, according to the safety strategy', '\n\nAll tanks and vessels containing flammable liquids shall have a deck bunding covering the tank perimeter controlling spreading of spills, and there shall be drainage within the bunding', '\n\nTanks collecting drains from hazardous areas shall be purged with inert gas to prevent explosive mixtures', ' Particular attention should be made to prevent spreading of fire water and drainage between fire areas, decks and lower escape ways']
71 | 9.4.2 Separation of drain systems | ['Closed and open drainage facilities shall be arranged so that they cannot affect each other adversely', '\n\nHazardous and non-hazardous open drains shall be physically separated to prevent backflow of hydrocarbons from hazardous to a non-hazardous area', '\n\nIf liquid from the hazardous and non-hazardous open drains are pumped to the same caisson or sump, the possibility of backflow into the non-hazardous open drain shall be prevented', '\n\nMeasures shall be implemented to prevent that vapors from the oily water treatment system enter the drainage systems, i', ' liquid seals shall be provided where the headers from open drain enter the collection tank(s), and these shall be designed for maximum possible back pressure', '\n \n\n\nCollection tanks shall be vented to an atmospheric vent system, and the outlet shall terminate at a safe location, i', '\n\nFire water and liquid spills on the helideck shall be drained in a safe, controlled and effective manner through a dedicated pipe drainage system', '\n\nThe open drain system shall provide effective means, e', ' Vent lines from seals shall be routed back to the area where the drains originate, or to a safe location', '\n\nThere shall be no connection between the drilling and production open drain systems', '\n\nTemporary storage of flammable liquids in tote tanks shall only be located in areas with an adequate collection and drain system']
72 | 9.5 Survivability requirements | ['The drain system, such as drain box and piping, shall not impair the integrity of fire divisions, see subclause 20']
73 | 10 Process safety system | []
74 | 10.1 Role | ['Process safety means of protection, including mechanical protection devices and safety instrumented functions, shall ensure that the process conditions do not exceed specified process safety limits']
75 | 10.2 Interfaces | []
76 | 10.3 Required utilities | []
77 | 10.4 Functional requirements | []
78 | 10.4.1 Process safety principles | ['The process safety functions shall provide a reliable and fast detection of process upsets and execution of the actions that are considered necessary to control the situation and avoid escalation', '\n\nFor topside functions, the PSD system shall be independent from the process control system', '\n\nFor subsea systems requiring PSD protection, the PSD function shall be independent of the subsea control system, i', '\n\nProcess and auxiliary systems shall be designed such that no single failure during operations can lead to unacceptable hazardous situations', ' The process safety system shall normally provide two levels of protection to prevent or minimize the consequences of an undesirable event within the process', ' If practicable, the two levels shall be provided by functionally different types of device', ' The design shall be in accordance with NORSOK P-002', '\n\nProcess safety layers of protection shall be established and designed in accordance with API RP 14C or ISO 10418 including referenced process standards that in a prescriptive manner often make recommendations of conventional solutions', '\n\nIn order to avoid cascading effect, the process shutdown shall be realized in accordance with ISO 10418,\n6', '\n\nWhere utilities, such as cooling water, are shared by process systems and equipment in non-hazardous areas, the utility system shall be designed to prevent migration of flammable liquids and gases into non- hazardous areas and systems', '\n\nLoss of instrument air or hydraulic supply (PALL) shall initiate a full production shutdown']
79 | 10.4.2 Process shutdown (PSD) valves | ['Shutdown valves on the liquid phase outlet from pressure vessels shall be located as close to the pressure vessel as possible, and the number of leak sources between the pressure vessel and shutdown valve shall be minimised', ' Shutdown valves shall have a fail-safe function under flowing conditions, i', '3related to fire design loads, it shall be defined as an ESD valve, reference is made to subclause 5']
80 | 10.4.3 Pressure safety valves (PSVs) | ['PSVs shall be designed, installed and maintained according to recognized international standards (API STD 520/521)']
81 | 10.4.4 Alarms, automatic actions | ['Alarms shall support operator decision-making during upsets and accidental situations', ' Actions shall be initiated automatically when process or equipment protection limits are exceeded']
82 | 10.4.5 Response time | ['The maximum response time of a process safety function to reach safe state on demand in actual operation shall be defined according to process dynamic behaviour', '\n\nTypical response times that shall be complied with unless faster responses are required from dynamic analysis:\n\n-Time from signal from sensor to start of PSD execution, e', ' de-energised solenoid valve, should be less than 2 seconds', '\n-PSD valve travel time (in service) should not exceed 2 seconds/inch (valve size) to reach safe state', ' For valves 8 inch or less, a typical travel time should be set to 15 seconds', '\n-New valves should have a design margin to allow for degradation during service life, typically 1 second/inch']
83 | 10.4.6 Logic solver | ['The logic solver (firmware, as standard manufacturer provision) shall be in compliance with IEC 61508/IEC 61511 and Norwegian Oil and Gas Association GL070']
84 | 10.4.7 Instrument based systems for secondary pressure protection | [' scenarios described in NORSOK P-002, the solutions shall be designed such that the annual frequency of overpressure above the temperature adjusted test pressure shall be less than 1x10-5', '\n\nThe annual frequency of overpressure above the code’s accepted pressure shall be less than 1x10-3', '\n\nThe secondary pressure protection system shall be realized independently from both the PSD and ESD systems', ' When applying the above requirements, the following leak frequencies should be applied:\n1)\tfor pressure lower than the code’s accepted pressure: p(leakage) = 0 (zero);\n2)\tfor pressure between the code’s accepted pressure and test pressure p(leakage) = 1x10-2;\n3)\tfor pressure above test pressure p(leakage) = 1']
85 | 10.5 Survivability requirements | [' If located in LER outside of the accommodation or utility area, consideration shall be made to\n \n\n\nthe consequences of loss of process feedback signals, e', 'The logic solver and essential utilities should be located as safe as possible in the accommodation or utility area', '\n\nIn case of RIO cabinets installed in hazardous areas, they should be located as safe as possible']
86 | 11 Emergency shutdown (ESD) | []
87 | 11.1 Role | []
88 | 11.1 Interfaces | []
89 | 11.3 Required utilities | []
90 | 11.4 Functional requirements | []
91 | 11.4.1 Manual ESD activation | ['Manual activation of the ESD system shall be possible from strategically positioned stations where accessibility and manning in a hazard situation is taken into account', '\n\nManual activation buttons shall be protected against inadvertent activation, e', ' Each activation button shall be clearly marked, and a consistent colour coding shall be applied for the activation buttons, e', ' UPS upon APS shall be executed via a timer independent of the logic solver, normally 30 min to ensure that necessary safety critical equipment is in operation during escape and evacuation', ' Separate function(s) shall be provided allowing bypassing timer based APS countdown', ' disconnecting the power to the ESD logic solvers, shall be included allowing safe shutdown upon failure of programmable logic', '\n\nSpecial consideration shall be made to disconnection of centralised escape lights such that no single fault shall result in disconnection of all escape lights', '\n\nPossibility for manual activation should be provided at strategic positions such as:\n\n-CCR (APS/ESD1/ESD2);\n-helideck (APS);\n-muster areas/lifeboat stations (APS);\n-bridge connections (ESD2);\n \n\n\n-drilling areas (driller shutdown and ESD2);\n-exits from process and wellhead areas (ESD2);\n-strategic located stations along escape routes (ESD2)']
92 | 11.4.2 Emergency shutdown (ESD) final elements | ['ESD valves shall isolate and sectionalise the process segments in a fast and reliable manner to reduce the total amount of released hydrocarbons in the event of a leak', ' ESD valves shall limit ESD segment volume in accordance with subclause 5', ' The valve arrangement shall be able to isolate at design flow conditions including consideration of increased flow from possible external leak, e', '\n\nThe following shutdown valves shall always be categorised as ESD valves:\n\n\uf0be\tvalves located in, or are the nearest shutdown valve to, a hydrocarbon riser;\no\tchemical injection to subsea wells do not require ESD valves topside provided that two independent well barrier elements in accordance with NORSOK D-010 are installed;\no\tchemical injection subsea at riser base, e', ' MEG and methanol for hydrate prevention during shutdown, shall be subject to special considerations and may require topside ESD or block valve (normally closed);\n\uf0be\tvalves located on the liquid outlet of large liquid vessels, such as separators and coalescers, see\n10', '2 for location of valves;\n\uf0be\tvalves located in a utility system where the consequences of valve failure with respect to safety may be significant, shall be subject to special consideration;\n\uf0be\twell isolation valves (DHSV, MV, WV, ASV, chemical injection, actuated annulus valves on gas lifted wells;\n\uf0be\tactuated SSIV (tagged as ESD valve)', '\n\nFor bridge connected installations with flow lines between the installations, considerations shall be made with respect to need for ESD valves related to worst credible process fire to stop flow between the installations', ' The main valve including actuator and related accessories such as pilot valve (“boost/quick dump”) and travel speed restrictor will be common, but shall have physically separate ESD/PSD activation signals and solenoids', ' The valves shall be tagged as ESD valves', '\n\nESD valves shall have either spring return or local accumulators to ensure fail-safe function under flowing conditions, i', ' Spring return type of valves shall be used when required size is available, normally 24 inches or less, as this is a more reliable fail-safe function compared to double acting valves', ' Local accumulators shall have 300 % capacity and should be placed as close as possible to the valve', '\n\nESD valves shall have defined criteria for leakage rates based on a study reflecting valve criticality', ' There shall be facilities for testing of internal leakage rate in the direction(s) the valve has a role', '\n\nESD valves, shall have local reset function', ' ESD valves shall be equipped with both remote and local position indication', ' hydraulic return and accumulator supply or means for valve travel time adjustment) shall be secured in correct position, e', ' Location of such valves should be considered with respect to area classification and should preferably be installed in hazardous area (process/wellhead area)', ' Local accumulators shall have 300 % capacity and should be placed as close as possible to the valve']
93 | 11.4.3 Emergency shutdown (ESD) actions | ['The ESD system shall activate all actions in accordance with the Safety Strategy', ' Consideration shall be given to interrelations between interconnected installations, e', '\n\nThe ESD functions shall be arranged in a tree-structured hierarchy, APS, ESD1 and ESD2', ' A higher ESD level shall initiate lower levels including PSD', '\n\nESD actions shall include depending on ESD level (see Figure 4):\n\n\uf0be\tshutdown of dry well trees, riser valves and subsea well trees when wells are located within the platform safety zone', '\n\nAny shutdown, spurious or intended, shall require a manual reset from CCR', '\nDuring well intervention DHSV and master valves shall be disconnected from the platform ESD system', ' It shall be possible to operate the DHSV and master valves in accordance with subclause 26', '\n \n\n\nLoss of ESD signals between an NNMI and remote control centre shall shutdown the NNMI upon a time delay', '\n\nESD of the remote control centre shall result in shutdown of the NNMI', '\n\nWhen installed, remotely operated Subsea Isolation Valves (SSIV) shall as a minimum be automatically closed upon APS activation and confirmed fire or gas detection in riser area', '\n\nThe X-mas tree valves part of the ESD function of well stream isolation shall, for subsea installations, apply a fail-to-safe principle for both electrical and hydraulic power supplies', '\n(d)\tThe start function shall be inhibited if gas has been detected in air intakes to generator, or generator has previously been tripped due to overspeed', '4) shall only initiate ESD2 and not automatic depressurization', ' Automatic\n \n\n\nEDP at confirmed gas detection shall be evaluated as a mean to limit extent and duration of possible gas leaks, ref subclause 12', '\n(f)\tAnnunciation (alarm and personnel warning) shall be given together with relevant shutdown level', ' General principles are shown in Figure 4 and should be used as basis for the facility specific safety strategy', ' The ESD hierarchy should be simple and unambiguous minimizing number of sub-levels', ' A signal on a certain level should never initiate shutdowns or actions on higher levels', ' The time delay should not exceed 10 min', ' Emergency board should be operative as long as possible to avoid need for start-up of emergency generator, ref']
94 | 11.4.4 Emergency shutdown (ESD) alarm annunciation | ['ESD system status shall continuously be available in CCR, and the system shall raise alarms in CCR for operator awareness or actions, considering:\n\n\uf0be\tESD level initiation;\n\uf0be\tESD function failure to execute actions upon demand;\n\uf0be\tESD function (sensor, logic solver or final element) defect or failure', '\n\nPersonnel shall be warned to ensure safe escape and evacuation, ref', ' Prepare to abandon alarm (at APS level) shall be initiated manually', ' Upon any confirmed ESD (auto or manual), general alarm shall be automatically initiated', ' Manual initiation of ESD1 or ESD2 level shall as a minimum initiate general alarm on affected platform', ' In addition the F&G system shall initiate automatic general alarm as described in clause 13 (Table 2) and clause 14 (Table 3)', '\n\nAn ESD alarm shall be alerted in other strategic locations, and announcement shall be made by means of and at typical locations such as:\n\n\uf0be\tVisual display of ESD alarms in drilling control room (driller’s cabin);\n\uf0be\tVisual display of ESD alarms in well intervention control station;\n\uf0be\tVisual display of ESD alarm (ESD2) in crane cabin']
95 | 11.4.5 Emergency shutdown (ESD) response time | ['Response time of all equipment and components included in the ESD function shall be defined', '\n\nStandardised response times shall be defined for groups of similar ESD functions except when individual ESD functions require exceptional response time to meet intended functionality', ' The time from ESD initiation to all XT barrier valves are in closed position (by sequential closure followed by power cut) shall be less than 4 minutes', ' Such delays shall however not be applied for wells located within the defined safety zone of the platform or if risk analysis has required well closure time which is shorter than achieved by the delay and ESD actuation time', '\n\uf0be\tApplied time delays associated with an ESD action to achieve safe state shall be clearly identified in relevant documentation, e', '\n\nTypical response times that should be complied with are:\n\n\uf0be\tTime from activation (ESD node receives signal) to start execution, e', ' de-energised solenoid valve, should normally be less than 2 seconds', '\n\uf0be\tThe total response time for closure of dry well tree (MV&WV) should not exceed 45 seconds', '\n\uf0be\tWith reference to topside ESD valves’ characteristics, the travel time (during lifetime) should not exceed 2 second /inch (valve size) to reach safe state', ' For valves 8” or less, a typical travel time of 15 seconds should be used', '\n \n\n\n\uf0be\tNew valves should have a design margin to allow for degradation during service life, typically 1 second/inch', '\n\nFor subsea facilities extended valve travel times are accepted due to special subsea design conditions:\n\n\uf0be\tThe total response time for closure of wet well tree (MV&WV via sequential closure) should not exceed 60 seconds', '\n\uf0be\tThe ESD shutdown should be delayed in order to allow a sequential closure of the well valves via subsea control facilities prior to the ESD disconnection of electrical power supply applying power cut and bleed off via normally energized “Quick dump” hydraulic valve', '\n\uf0be\tThe total response time for closure of SSIVs should be maximum 2 minutes unless risk analysis has required a shorter valve closure time']
96 | 11.4.6 Logic solver | ['The logic solver (firmware, as standard manufacturer provision) shall be in compliance with IEC 61508/IEC 61511 and Norwegian Oil and Gas Association GL070']
97 | 11.4.7 Emergency shutdown (ESD) independence | ['The ESD system shall operate as an independent system', ' Prerequisites to fulfil the independence requirements are:\n\n\uf0be\tESD safety related functions shall be realised in addition to and independent of the PSD and PCS functions, but the ESD system units (logic solver) can be an integral node of the overall SAS', '\n\uf0be\tESD system units (logic solver) shall only be used for ESD related safety functions', ' process tapping, impulse lines, air supply branch-off and power fuses) shall be separate from other functions, directly connected to ESD system unit', '\n\uf0be\tESD final element shall be operated directly from ESD system unit, but such devices may in addition be operated by other safety related systems if they have separate activation devices e', '\n\uf0be\tAn appropriate level of independency shall be obtained for ESD functions (final element) if they are integrated within remote/local panels, e', ' This realisation shall be subject to given prerequisites as described in Norwegian Oil and Gas Association GL070']
98 | 11.5 Survivability requirements | ['The logic solver and essential utilities shall be located as safe as possible in the accommodation or utility area', ' With respect to retrofits and extensions, the ESD system, logic solver and essential utilities shall not be located less safe than existing logic solvers, i', '\n\nFinal elements shall resist accidental loads such as explosion, fire and falling loads where applicable, e', '\n\uf0be\tESD valves shall remain in safe position throughout the duration of the accidental scenario, i', '\n\nESD valves shall be in accordance with recognized standard regarding fire resistance, e']
99 | 12 Emergency depressurisation and Flare/Vent system | []
100 | 12.1 Role | []
101 | 12.2 Interfaces | []
102 | 12.3 Required utilities | []
103 | 12.4 Functional requirements | []
104 | 12.4.1 Emergency depressurisation | ['The EDP system shall ensure that the process is depressurised in a fast and reliable manner in order to avoid unacceptable rupture and to minimize leak durations', ' The EDP shall in combination with all other risk reducing measures, contribute to a reduction of the fire and explosion risk to:\n\n\uf0be\tavoid instantaneous release (rupture and leakage) of large volumes of flammables;\n\uf0be\tavoid escalation of fire between areas/units and during escape/rescue by reducing internal pressures, fire load and duration', '\n\nThe EDP rate and times shall be set based on a study reflecting the risk on the specific installation and principles in API STD 521', ' EDP times shall be in accordance to specified requirements for protection of pressurised systems exposed to fire', '\n\nThe following aspects shall be considered in the design process:\n\n\uf0be\tdamage to internals of equipment (e', ' trays, packing supports), entrainment of packing or catalyst into the depressurization system;\n\uf0be\tthe depressurisation rates shall be maximized within a defined level of flare system utilisation to reduce risk further and minimize the need for passive fire protection', '\n\nFailure of a segregation valve impacting EDP segments shall not result in overpressure of the flare system', '\n\nIn case sequential EDP is required, the time delay and/or sequence to open EDP valves shall ensure that the flare system capacity is not exceeded and failure in the sequence shall not lead to rupture of the flare system', '\n\nThe EDP valves shall be treated similarly to ESD valves with respect to logic, tagging, response time etc', ' The EDP valves shall be equipped with position indication (remote and local) and have fail-safe open function', ' All pressure vessels and piping segments, which during shutdown contain more than\n \n\n\n1 000 kg of hydrocarbons (liquid and/or gaseous), shall be equipped with a depressurising system', ' Liquid that may accumulate between the EDP valve and the orifice shall not freeze', '\n\nBlock valves in EDP lines shall be secured open', '\n\nAll process segments without EDP shall be clearly marked on the P&IDs', ' Analysis regarding material capacity versus EDP should be performed as specified in “Guidelines for protection of pressurised systems exposed to fire”, Report 27', ' For pressure vessels and piping segments without a depressurising system, containing gas or unstabilised oil with a high gas/oil-ratio, the maximum containment should be considerably lower, typically less than\n100 kg']
105 | 12.4.2 Activation of emergency depressurisation (EDP) | ['EDP shall be automatically initiated upon confirmed fire detection in hazardous areas (process, riser and wellhead areas), on fire and gas detection in riser and wellhead areas and on gas detection when deluge is activated (a gas leak is almost impossible to locate when deluge is released)', ' Any delay of opening of EDP valves shall be accounted for in evaluations of rupture of process equipment due to fire exposure', '\n\nFull platform depressurisation shall be possible in CCR (operator station and dedicated push button\nin CAP)', ' Manual push buttons shall be protected against inadvertent activation, e', ' Use of the dedicated push buttons shall also initiate ESD2', '\n\nAutomatic EDP at confirmed gas detection shall be evaluated as a mean to limit extent and duration of possible gas leaks']
106 | 12.4.3 Flare, vent and knock out drum | ['\n\nFlare:\n\nFlare shall be located and designed to ensure that the heat radiation level at maximum or continually release rate will be within acceptable limits in all areas of the installation', ' The permissible radiation levels for personnel exposure shall be in accordance with API STD 521', '\n\nCold and local vents:\n\nVents shall be terminated at a safe location, normally verified by gas dispersion simulations', ' Operational conditions that may give gas heavier than air shall be included', '\n\nGas concentrations from vents (or extinguished flare) shall not exceed 20 % LEL in any area on the installation where ignition of the release is possible', ' Helicopter flight paths shall be optimized and based on dispersion studies of release from extinguished flares, ref', '\n\nUnintentional ignition of the vents shall not give unacceptable heat loads', ' Consideration should be made to effect of clothing', '\n\nLocal venting of hazardous gases should not be permitted unless it can be done without hazard to the personnel (including occupational health) or the installation']
107 | 12.5 Survivability requirements | ['The flare system shall withstand explosions and fires for the required period of time to minimum maintain integrity to avoid unacceptable rupture, ref', ' Special consideration shall be given to flanges, pipe supports, pipes with no flow during EDP (e', ' Use of pipe specification that can resist the loads should be considered as an alternative to avoid PFP']
108 | 13 Gas detection | []
109 | 13.1 Role | ['The gas detection system shall monitor continuously for the presence of flammable or toxic gases, to alert personnel and allow control actions to be initiated manually or automatically to minimise the probability of personnel exposure, explosion and fire']
110 | 13.2 Interfaces | []
111 | 13.3 Required utilities | ['Gas detection system performance is dependent on uninterruptible power supply (UPS) to keep the gas detection operational should main electrical power supply fail']
112 | 13.4 Functional requirements | []
113 | 13.4.1 Design coverage | ['The gas detection function shall provide reliable and fast detection of flammable and toxic leaks before a gas cloud reaches a concentration and size which could cause risk to personnel and installation', ' type and location of detectors) shall be established according to relevant gas characteristics (e', '\n\nDetectors shall be installed based on a study of gas leakage scenarios within each area considering leakage sources and rate, dispersion, equipment arrangement and environmental conditions such as ventilation, and the probability of detection of small leakages within the area', ' access ways/walkways along flow direction, shall be covered', '\n\uf0be\tWhere relevant, detectors shall be positioned at different heights in an area including coverage of different natural flow paths', '\n\uf0be\tConsideration shall be given to gases both lighter and heavier than air including temperature effects from the release', ' for noise suppression, shall be subject to special consideration', '\n\nA combination of open path/line detectors and point detectors shall be used to optimize the coverage and detection probability', '\n\n\uf0be\tHydrocarbon detectors, preferably IR detectors, with provisions of self-diagnostics and suited for the gas to be detected shall be used', '\n\nThe basis and assumptions used for detector selection and location shall be documented', '\n\nThe detector grid coverage described above may be optimized, typically in wellhead and process areas, possibly achieving a reduction in no of detectors, by applying the following method and target:\n\nTarget: A gas cloud equal to the volume of the dimensioning gas cloud (explosion loads) shall be detected with a 95 % probability for confirmed detection on two detectors', '\n\nIn addition, the objective shall be to provide effective detection of smaller leaks than above to give a warning (alarm), typically a leakage rate of 0,1 kg/s', '\n\nSeparate sensors and alarm handling shall be provided for detection of toxic gases (e', ' For such detection, attention shall be given to the fact that hazardous effects to people and explosion hazard may be directly linked to both concentration and exposure time', ')\n\nTemporary units and equipment shall be covered by gas detection in accordance with the principles in this document', ' Areas where such equipment will be located shall have connections to the platform’s Fire & Gas system', "\n\nThe following principles should be applied for determination of location of detectors:\n \n\n\n\uf0be\tNatural flow 'corridors', e", '\n\uf0be\tCatalytic detectors should only be used if proper detection performance by other types is not achieved', '\n\nDetector coverage should primarily be achieved using open path / line detectors and supplied with point detectors where adequate coverage cannot be achieved with open path / line detectors', ' For conversion between open/path line and point detectors the following formula may be applied:\n\nNp = (Ls * CLEL) / (LELm * 100)\nWhere\nNp\tNumber of point detectors Ls\tLength of line of sight (m)\nCLEL\tLow alarm limit point detectors (% LEL)\nLELm\tLow alarm limit open path/line detectors (LELm)\n\nFor confirmed detection of flammable gases in hazardous areas, using 20 % LEL level, a gas cloud of 10 meters in diameter should be detected anywhere in the area', ' Dispersion studies should be performed for verification and optimization of location and number of detectors', ' To determine the necessary number of point detectors in an area, the size of the dimensioning gas cloud should be used', '\n\nFor detection of vapours from process liquid releases, the following principles should apply;\n\n\uf0be\tlow-level detectors (heavy gas), but normally not located lower than 0,5 meters above ground level;\n\uf0be\tdetectors arranged in 5 meters triangular grid around potential source of release']
114 | 13.4.2 Gas detection location – Areas requiring gas detection | ['Gas detectors shall be provided in all areas where potentially dangerous/toxic gas concentrations may be present', '\n\nAs a minimum the following areas shall be covered by HC detectors:\n\n\uf0be\tzone 1 and zone 2 areas;\n\uf0be\tventilation air inlets;\n\uf0be\tventilation outlet from hazardous areas (except paint containers and small noise enclosures)\n\uf0be\tcombustion air intakes and turbine hoods/enclosures air inlet/outlet;\n\uf0be\trooms that contain possible ignition sources and are arranged with openings towards a hazardous area, ref', '4 for further details;\n\uf0be\tfor floating units such as FSU and FPSO, gas detection shall be provided in areas such as ballast tanks and cofferdams where gas may migrate through small cracks towards cargo tanks etc', ' Aspiration gas detector systems shall be considered for such applications', '\n\nH2 detection shall be installed in battery rooms unless it can be documented that sufficient quantities of hydrogen cannot be generated to pose a danger', '\n\nOxygen deficiency detection shall be provided in areas where a low O2 concentration may be present, e', '\n\nOil mist detectors (optical obscuration) shall be considered used in areas with a risk of leak from pressurised liquid utility systems like diesel oil, hydraulic oil, lube oil etc', '\n\nArrangements and actions associated with gas detection should be implemented as described in Table 2']
115 | 13.4.3 Gas detection actions and voting | ['The gas detection system shall initiate actions in accordance with the principles below and the Safety Strategy', '\n\nAutomatic initiation of actions shall include:\n\n\uf0be\temergency shutdown (confirmed gas detection);\n\uf0be\tignition Source disconnection;\n\uf0be\tHVAC shutdown (single low gas detection at air intake);\n\uf0be\tdeluge activation in naturally ventilated areas to reduce explosion overpressure/drag forces if specified in Safety Strategy (confirmed gas detection);\n\uf0be\tEDP activation if specified in safety strategy (confirmed gas detection in hazardous area);\n\uf0be\tstart of fire water pump when used for explosion mitigation (low gas detection);\n\uf0be\tgeneral alarm (confirmed gas detection)', '\n\nConfirmed gas detection and applied voting principles shall comply with the following:\n\n\uf0be\t2ooN detector to reach specified alarm limit when N ≥ 3 should be based on low alarm limits (ref', '\n\nThe number of detectors that may simultaneously be inhibited or in fault shall be assessed addressing issues such as area risk, area detection coverage, out of operation duration and compensatory measures including local area safety guards', ' Prerequisites and measures required in the case of detectors are inhibited or faulty shall be part of the operating instructions', '2, non-\nessential (A)\tNA\t(A) Action on confirmed gas to be specified in safety strategy\n \n\n\nArea/room\tDetector location\tGas detection (note f)\tAlarm type (note d)\tAutomatic Shutdown\tHVAC action\tComments\nNotes\n\na\tFor mechanically ventilated areas special consideration shall be made, ref', '\nc\tGroup 3 equipment shall not be located in rooms safe by ventilation, ref', ' Special consideration shall be made for LER in turret area', ' Group 3 equipment in such rooms shall be fitted with air locks and as a minimum be disconnected upon loss of ventilation in combination with gas detection in air lock', '\nd\tAlarms presented in CCR shall also be presented as a not area specific general gas alarm in other strategic location such as crane cabin, drillers cabin and office and jack-ups', '\nf\tLifts shall not be considered as a part of escape routes', ' However, it shall be possible to escape from the lift at any elevation', ' Lifts shall automatically go to next floor level and stop upon single gas detection\n', '\n\nConfirmed gas detection and applied voting principles shall comply with the following:\n\n\uf0be\t2ooN detector to reach specified alarm limit when N ≥ 3 should be based on low alarm limits (ref', '\n\uf0be\tVoting should include all detectors within a detection area (any type of detectors)', ' When deluge is automatically released, EDP should also be automatically activated', '\n\n1oo1 detection principle should only be used for area monitoring and alarms', '\n\nArrangements and actions associated with gas detection should be implemented as described in Table 2', ' When deluge is automatically released, EDP should also be automatically activated']
116 | 13.4.4 Requirements for HC gas detection at air intakes | ['Air intakes shall be monitored for presence of gas, preferably by IR type detection', '\n\nThe number and location of detectors shall be selected and installed to cover the cross-sectional area of the air intake or air inlet channel since gas concentration may not be homogenous over the inlet / channel cross-sectional area', '\n\nApplied low gas alarm shall be equal to or lower than 10 % LEL (or equivalent for open path detectors, i', '\n\nApplied high gas alarm shall be equal to or lower than 30 % LEL (or equivalent for open path detectors,\ni', '\n\nLow gas alarm (single detector) at the intake shall initiate shutdown of fans, dampers and electric heaters', '\n\nConfirmed gas detection (2ooN) should be based on one detector at low alarm and one detector at high alarm, i']
117 | 13.4.5 Gas detection set-points | ['detection (extract and area) the alarm limit shall be 10 % LEL', '\n\uf0be\tLow alarm set-point for IR open path / line detector shall be maximum 1 LELm', '\n\uf0be\tHigh alarm set-point for point detectors shall be maximum 30 % LEL', ' For turbine enclosure detection the alarm limit shall be 15 % LEL (extract and area)', '\n\uf0be\tHigh alarm set-point for IR open path/line detector shall be maximum 2 LELm', '\n\nIf toxic gas detection is required, separate outputs for annunciation of toxic gas alarm shall be provided', ' The following alarm limits for toxic gas shall be used:\n \n\n\nH2S gas detection:\n\n\uf0be\tLow alarm set point shall be maximum 5 ppm (assume area inspection and reporting within 15 minutes)', '\n\uf0be\tHigh alarm set point shall be maximum 50 ppm (immediate area evacuation, 50 % of standard IDLH value)', '\n\nCO2 gas detection:\n\n\uf0be\tLow alarm set point shall be maximum 5 000 ppm', '\n\uf0be\tHigh alarm set point shall be maximum 15 000 ppm', '\n\nCO gas detection:\n\n\uf0be\tLow alarm set point shall be maximum 100 ppm (assume area inspection and reporting within 15 minutes, reference standards allows 25 ppm for 8 hours)', '\n\uf0be\tHigh alarm set point shall be maximum 600 ppm (immediate area evacuation, 50 % of standard IDLH value)', '\n\nO2 deficiency detection (see IEC 60079-29-2):\n\n\uf0be\tLow alarm set-point shall be minimum 19,5 vol %', '\n\uf0be\tLow-low alarm set-point shall be 19,0 vol %']
118 | 13.4.6 Gas detection alarms | ['F&G system status shall be continuously available in CCR, and the system shall raise alarms in CCR for operator awareness or action, considering:\n\n\uf0be\tGas detection\n\uf0be\tFailure to execute action upon demand\n\uf0be\tFunction (sensor, logic solver, final element) defect or failure', '\n\nStatus/alarm parameters for each individual gas detector shall be identifiable in the CCR', ' Gas alarms shall also be announced at other strategic locations, e', '\n\nFor alarms from detectors located in drilling areas the information presented in CCR should be mirrored in drillers cabin and drillers control office']
119 | 13.4.7 Gas detection response time | ['Maximum response time of the gas detection function shall be defined in order to ensure that total reaction time for each safety function can be fulfilled', '\n \n\n\nThere shall be no predefined delays of actions initiated upon gas detection unless a delay is safer', ' In such a case, this shall be clearly identified in relevant documentation such as FPDS and C&E diagrams', '\n\nFor gas detection in ventilation inlets IR type detector shall be located as close as possible to the inlet to ensure fast detection', '\n\nTypical response times that should be complied with unless faster responses are specified elsewhere:\n\n\uf0be\tIR detector response time (T90) should be less than 5 s for general area applications, and less than 2 s if used in HVAC ducting', '\n\uf0be\tthe time from detector alarm limit is reached until alarm is presented on operator station and start of action should be less than 2 s']
120 | 13.4.8 Gas detection logic solver | ['The logic solver (firmware, as standard manufacturer provision) shall be in compliance with IEC 61508/ IEC 61511 and Norwegian Oil and Gas Association GL070']
121 | 13.4.9 Independence | ['The F&G safety related functions shall fulfil their intended role independently of other control - and safety related control systems', ' Prerequisites to fulfil the independence requirements are:\n\n\uf0be\tF&G safety related functions shall be realised in addition to and independent of installation basic control systems', '\n\uf0be\tF&G system units (logic solver) shall only be used for F&G related safety functions', ' air supply branch-off and power fuses) shall be separate from other functions that are directly connected to F&G system unit', '\n\uf0be\tF&G final element shall be operated directly from F&G system unit', ' “All action signals, except release of firefighting systems (deluge, foam, watermist etc), shall be normally energized', ' Disconnection of ignition sources should be realized through the ESD system']
122 | 13.5 Survivability requirements | ['The logic solver and essential utilities shall be located as safe as possible in the accommodation or utility area', ' With respect to retrofits and extensions, the, logic solver and essential utilities shall not be located less safe than existing logic solvers, i']
123 | 14 Fire detection | []
124 | 14.1 Role | ['The fire detection system shall monitor continuously for the presence of a fire to alert personnel and allow control actions to be initiated manually or automatically to minimise the likelihood of fire escalation and probability of personnel exposure', '\n\nThe early fire detection system shall, relevant to specific equipment and areas, monitor continuously for the presence of an incipient fire condition to alert personnel and allow control actions to be initiated manually to minimise the probability of a fire condition to develop']
125 | 14.2 Interfaces | []
126 | 14.3 Required utilities | ['Fire detection system performance is dependent on uninterruptible power supply (UPS) to keep fire detection operational should main electrical power supply fail']
127 | 14.4 Functional requirements | []
128 | 14.4.1 Design coverage | ['The fire detection function shall provide reliable and fast detection of a fire by adequate type, number and location of fire detectors and shall ensure timely alarm and initiation of control actions', '\n\nDetectors shall be provided based on an evaluation of fire scenarios within each area considering potential fire sources and characteristics, consequences, area and equipment arrangement and environmental conditions', '\n\nFire detection coverage in each area shall be based on flame size, smoke characteristics and temperature (heat) rise', '\n\nWhen suitable according to area conditions and fire characteristics, flame detectors shall be given preference over heat sensors', '\n\nThe basis and assumptions used for detector selection and location shall be documented', ' The location of smoke detectors in LERs and critical rooms shall be confirmed by smoke dispersion tests for actual conditions inside the rooms with ventilation operative', ' Scenarios to be detected and performance requirements shall be defined in the Safety Strategy', ' for noise suppression, shall be subject to special consideration', '\n\nEarly warning smoke detection systems, sensitive to small concentration of combustion products, should be considered in rooms containing live electrical equipment and where firefighting is based upon local inspection and manual intervention including disconnection of relevant electrical equipment', ' One detector should be located at the HVAC extract points']
129 | 14.4.2 Fire detection location – areas requiring fire detection | ['All areas on the installation shall have suitable means of fire detection', ' Fire detection shall as a minimum be in accordance with Table 3', '\n\nDetectors in one fire area shall not detect fires in adjacent fire areas and thereby cause unintended automatic release of fire water which may exceed the dimensioning fire water capacity', '\n\nFlame detectors shall be located in a manner that minimises the likelihood of false fire alarms being initiated, e', '\n \n\n\nFlame detectors should be the primary means for detection of fires in hazardous areas']
130 | 14.4.3 Manual call points | ['Manual Call Points shall be located strategically, and in locations such as:\n\n\uf0be\talong escape routes;\n\uf0be\tinside buildings such as offices etc', '\n\nThe maximum walking distance to a manual call point should not exceed 30 m', ' Manual call points should be protected against inadvertent activation']
131 | 14.4.4 Characteristics and calibration | ['Detector characteristics and calibration (pre-set sensitivity) shall ensure detection of a fire condition at an early stage, and the detector shall be capable of operating under the conditions at the time that fire detection is needed', '\n\nFire detectors shall be self-monitoring and should include provisions of self-diagnostic to the extent available', '\n\nFlame detectors shall comply with actual fire potential and environment conditions within the relevant area e', '\n\nHeat point detectors (electrical) characteristics shall comply with actual fire potential and environmental conditions within the relevant area, e', '\n\nSmoke detectors characteristics shall comply with actual fire potential and environmental conditions within the relevant area, e', ' explosive fire in high voltage switchgear;\n\uf0be\tsmoke detectors located in areas such as suspended ceilings and raised floors shall have remote indication on VDU;\n\uf0be\tearly warning sensor specified with higher sensitivity (0,4 % to 0,8 % light obscuring per metre) than norm recommendation;\n\uf0be\tmaximum distance between sensors 11 m, maximum distance from sensor to bulkhead 5', '\n\nFire detectors shall be self-monitoring and should include provisions of self-diagnostic to the extent available', ' Based on a typical flame detector characteristic, the distance between flame detectors and targets monitored should not exceed 26 m;\n\uf0be\tsensor direction and angle;\n\uf0be\tsensitivity to external impact such as arc welding and burner boom']
132 | 14.4.5 Fire detection actions and voting | ['\n\nA fire alarm shall be raised upon activation of any fire detector, and confirmed fire should be based on voting between two or more fire detectors in alarm', ' Confirmed fire detection and applied voting principle for automatic actions shall be defined in the Safety Strategy', ' Smoke detectors covering enclosures and their HVAC inlets shall not be voted together', '\n\nThe number of detectors that may simultaneously be inhibited or in fault shall be assessed addressing issues such as area risk, area detection coverage, out of operation duration and compensatory measures including local area safety guards', '\n \n\n\nPrerequisites and measures required in the case of detectors are inhibited or faulty shall be part of the operating instructions', ' Manual, release shall be possible in the fire scenario', '\nb\tAlarms presented in CCR shall also be presented as a not area specific general fire alarm in other strategic location such as crane cabin, drillers cabin and office and jack-ups', '\n\nA fire alarm shall be raised upon activation of any fire detector, and confirmed fire should be based on voting between two or more fire detectors in alarm', '\n\nThe following voting principles should generally apply:\n\n\uf0be\tSmoke (except areas such as accommodation):\no\t2ooN detectors to reach specified alarm limit when N ≥ 3\nNOTE\tSmoke detectors are less likely to be used together with other types of fire detectors, and applications that require voting are not common', '\n\n\uf0be\tFlame:\no\t2ooN detectors to reach specified alarm limit when N ≥ 3\n\uf0be\tHeat:\no\t1ooN detectors to reach specified alarm limit when N ≥ 2\nVoting should include all fire detectors within a detection area exposed to the same fire scenario', '\n\n1oo1 detection principle should only be used for area monitoring and alarms', '\n\nArrangements and actions following associated with fire detection should be implemented as described in Table 3', '\n\nTable 3 — Fire detection principles\n\n\nArea/room\tType of\ndetection (note a)\t\nAlarm type (note b)\t\nAutomatic shutdown/ EDP\t\nAutomatic AFP\t\nHVAC\ninterface\t\nComments\nWellhead area\n(Naturally ventilated)\tFlame Alarm\tCCR\tNone\tStart FW pump\tNA\t\n\tFlame Confirmed\tCCR + GA\tESD2 + EDP\n+ ASV + DHSV\tRelease deluge\t\t\nRiser area\tFlame Alarm\tCCR\tNone\tStart FW pump\tNA\t\n\tFlame Confirmed\tCCR + GA\tESD2 + SSIV +EDP\tRelease deluge\t\t\nHC process area\tFlame Alarm\tCCR\tNone\tStart FW pump\tNA\t\n(Naturally ventilated)\tFlame Confirmed\tCCR + GA\tESD2 + EDP\tRelease deluge\t\t\nHC process area\tFlame Alarm\tCCR\tNone\tStart FW pump\tNo action\t\n(Mechanically ventilated)\tFlame Confirmed\tCCR + GA\tESD2 + EDP\tRelease deluge\tClose damper and fans\t\nUtility areas\n(Hazardous naturally ventilated)\tFlame Alarm\n\nFlame Confirmed\tCCR\n\nCCR + GA\tNone ESD2 (A)\tStart FW pump\n\nRelease deluge/sprin kler\tNA\t(A) ESD2 if not otherwise specified in Safety Strategy\nUtility areas\n(Non- hazardous naturally\nventilated)\tFlame(A) Alarm\tCCR\tNone\tStart FW pump\tNA\t(A) For areas without flammable liquids other detection means such as camera or smoke detection should be considered', '\n\tFlame confirmed\tCCR + GA\tESD2 (A)\tRelease AFP(A)/(B)\tClose damper and fans\t\nUtility areas\n(Non- hazardous mechanically ventilated)\tFlame(A) Alarm\tCCR\tNone\tStart FW pump\tNo action\t(A)\tFor areas without significant flammable liquid volumes other detection means such as camera or smoke detection should be considered', ' low risk other detection means such as camera or smoke detection should be considered', '\n(D)\tFire doors kept open with magnetic devices should be closed on single smoke in indoor areas\n\tSmoke 2ooN(A)\tCCR + GA\tNone\tNone(B)\tMaintain ventilation/ active smoke control(C)\t\nLQ (common areas)\tSmoke Alarm\tCCR\tNone(C)\tNone(A)\tMaintain ventilation/ active smoke control(B)\t(A)\tProvided amount of flammable material is sufficiently low ref', '\n(C)\tFire doors kept open with magnetic devices should be closed on single smoke in indoor areas\nVent extract from galley\tHeat Alarm and Confirmed\tCCR\tNone\tRelease AFP(A)\tManual shutdown\t(A) AFP may be foam, water mist or gaseous systems']
133 | 14.4.6 Fire detection alarms | ['F&G system status shall be continuously available in CCR, and the system shall raise alarms in CCR for operator awareness or action, considering:\n\n\uf0be\tdetection of fire or activation of Manual Call Point;\n\uf0be\tfailure to execute action upon demand;\n\uf0be\tfunction (sensor, logic solver, final element) defect or failure', '\n\nStatus/alarm parameters for each individual fire detector shall be identifiable in the CCR', '\n\nAn F&G alarm condition shall be alerted in other strategic locations, and announcement shall be made by available means of and at typical locations such as:\n\n\uf0be\tdrillers cabin and office;\n\uf0be\tcrane cabin;\n\uf0be\tjack-ups', '\n \n\n\nLoss of communication with or defects of the fire detection central shall give alarm in CCR', '\n\nFor alarms from detectors located in drilling areas the information presented in CCR should be mirrored in drillers cabin and office']
134 | 14.4.7 Response time | ['Response time of the fire detection function shall be considered and documented in the Safety Strategy', '\n\nStandardised response times shall be defined for groups of similar F&G functions except when individual F&G functions require exceptional response time to meet intended functionality', '\n\nThere shall normally be no predefined delays of fire detection']
135 | 14.4.8 Logic solver | ['The logic solver (firmware, as standard manufacturer provision) shall be in compliance with\nIEC 61508/ IEC 61511 and Norwegian Oil and Gas Association GL070']
136 | 14.5 Survivability requirements | ['The logic solver and essential utilities shall be located as safe as possible in the accommodation or utility area', ' With respect to retrofits and extensions, the, logic solver and essential utilities shall not be located less safe than existing logic solvers, i', '\n\nCabling of fire detectors shall be routed such that the likelihood of damage due to external accidental loads and simultaneous loss of detection in several detection areas is minimized', ' Fire resistant cables shall be applied']
137 | 15 Ignition source control (ISC) | ['The ignition probability of flammable liquids and explosive gas atmospheres shall be minimized by rendering the sources of ignition harmless or reducing the likelihood of occurrence of effective ignition sources']
138 | 15.1 Role | []
139 | 15.2 Interfaces | []
140 | 15.3 Required utilities | []
141 | 15.4 Functional requirements | []
142 | 15.4.1 General | ['\n\nArea classification shall be established in accordance with IEC 61892-7 and IEC 60079-10-1 or EI 15', '\n\nA systematic mapping of all potential ignition sources both electrical and non-electrical, shall be performed, including risk assessment and implementation of necessary risk reduction measures in order to reduce ignition probability of an explosive atmosphere occurring in both hazardous and non- hazardous areas', ' The equipment shall be categorized as non-essential, essential and safety critical equipment respectively', '\n\nEquipment shall be constructed, installed, operated and maintained in accordance with ATEX requirements (see FOR-1996-12-09-1242 [6]) and standards IEC 61892 and ISO 80079-36', ' The equipment shall be certified by an accredited test institution according to, as a minimum, the lowest explosion protection level accepted for use in the particular zone by the reference standard', ' The equipment in question shall, as a minimum, be supported by a declaration of conformity which is verified by an independent documented review', ' fan, damper and heaters) and outlets shall, as a minimum, comply with a level of explosion protection according to hazardous area zone 2 requirements', ' If not available, the equipment shall be disconnected in accordance with the principles below', '\n\nPossible technical malfunction of Ex equipment shall be taken into account', '\n\nCombustion type of equipment that may cause an ignition hazard due to flames, hot gases or hot particles shall not be installed in hazardous areas', ' Irrespective of location, diesel engines shall be provided with flame arrestor in the combustion inlet, overspeed protection (close combustion air damper and fuel valve) and spark arrestor', ' If located in a mechanically ventilated room, the combustion air shall be taken from non-hazardous area outside the room and minimum 3 m from any zone 2 boundaries to reduce ignition probability', '\n \n\n\nElectrical isolation shall be defined as disconnection of the power feeder cable at the distribution boards', '\n\nUse of temporary equipment connected to EX socket outlets which is not subject to trip on low gas alarm/ESD 2, shall have appropriate marking to ensure that equipment is disconnected according to the principles in this clause', '\n\nBoost charging of batteries shall be stopped automatically upon loss of ventilation in the battery room or detection of hydrogen gas in the room', ' To reduce explosion risk as far as practical, also Ex-equipment should be electrically isolated on relevant gas detection', ' For simplification and reliability of the isolation function, the numbers of breakers to be tripped should be minimized, e']
143 | 15.4.2 Non-essential equipment (electrical and non-electrical) | []
144 | 15.4.2.1 General | ['\n\nAll group1 equipment located in hazardous and non-hazardous naturally ventilated areas shall be disconnected on single low gas alarm anywhere on the installation and on ESD2 initiation', ' EX outlets that support temporary equipment which is not subject to trip on low gas alarm/ESD 2, shall have appropriate marking and use shall be governed by the permit to work system', '\n\nNon-essential Ex-equipment may also be disconnected on single gas detection, but shall as a minimum be disconnected on confirmed gas detection and ESD2 initiation']
145 | 15.4.2.2 Hazardous areas: | ['Ex equipment shall be used in accordance with the general principles in subclause 15']
146 | 15.4.2.3 Non-hazardous naturally ventilated areas: | ['Equipment shall minimum be suitable for Zone 2 in accordance with the general principles in subclause 15']
147 | 15.4.2.4 Non-hazardous mechanically ventilated areas: | ['Non-explosion protected equipment (Group 1), both electrical and non-electrical, installed inside non- hazardous, mechanically ventilated rooms shall be automatically tripped and electrically isolated as follows:\n\n\uf0be\tOn single gas detection in ventilation intake', ' due to doors associated with workshops, the equipment shall be disconnected on single low gas alarm anywhere on the installation and/or ESD2']
148 | 15.4.3 Essential equipment (electrical and non-electrical) | []
149 | 15.4.3.1 General | []
150 | 15.4.3.2 Hazardous areas: | ['Ex equipment shall be used in accordance with the general principles in subclause 15', '\n\nEssential Ex equipment should be tripped on ESD 2 in order to reduce the ignition probability', ' If not tripped on ESD 2, it should be tripped on confirmed gas detection', ' Particular consideration should be made to possible negative consequences for equipment essential for drilling / well related activities']
151 | 15.4.3.3 Non-hazardous naturally ventilated areas | ['Equipment shall minimum be suitable for Zone 2 in accordance with the general principles in subclause\n15', '\tIf not available, such equipment shall be tripped on ESD2']
152 | 15.4.3.4 Non-hazardous mechanically ventilated areas | ['Non-explosion protected equipment (Group 2), both electrical and non-electrical, installed inside non- hazardous, mechanically ventilated rooms shall be automatically tripped and electrically isolated as follows:\n\n\uf0be\ton confirmed gas detection in ventilation intake;\n\uf0be\tby defined ESD level (manually or automatically initiated, see 11', ' Note; all equipment within air lock shall be in accordance with the area classification outside', ' If restoration cannot be realised within reasonable time, instruction and means shall be available for disconnection of ignition sources in the room', '\n\uf0be\tInstructions to restart power supply in room following loss of ventilation/electrical disconnection shall be available, e', ' sensors and actuators, shall be minimum suitable for Zone 2 including those installed inside non-hazardous rooms']
153 | 15.4.4 Safety critical equipment (electrical and non-electrical) | []
154 | 15.4.4.1 General | ['\n\nSafety critical equipment not shutdown by an APS (after initiation plus time delay) shall irrespective of location comply with hazardous area zone 1 requirement if located outdoors', '\n\nThe emergency generator shall be tripped immediately upon APS (no time delay)', ' Equipment supplied from UPS shall meet the following:']
155 | 15.4.4.2 Hazardous area: | ['Equipment located in such areas shall meet relevant zone requirements and shall be tripped after time delayed APS']
156 | 15.4.4.3 Non-hazardous naturally ventilated areas: | ['Equipment located in such areas shall meet minimum zone 2 and shall be tripped after time delayed APS']
157 | 15.4.4.4 Non-hazardous mechanically ventilated areas: | ['Non-explosion protected electrical equipment (safety critical category – group 3) shall be installed in enclosed mechanically ventilated rooms', '\n\nAll active field equipment such as detectors and loudspeakers shall be minimum suitable for Zone 2 including those installed inside non-hazardous rooms and areas such as LQ', '\n\nMeans for shutdown of safety critical equipment shall be provided as follows:\n\n\uf0be\tby activation of APS with a predefined time delay;\n \n\n\n\uf0be\tinstantaneous disconnection by manual activation from manned area/room, i', '\n\nFire water pump arrangement including diesel engines, electrical generator and motors, shall:\n\n\uf0be\tmeet requirements for diesel engines given in 15', '1,\n\uf0be\tbe automatically tripped only by overspeed (close damper and fuel supply valve) if not in test mode, and\n\uf0be\tbe stopped manually (local) only (shall not be automatically stopped by APS)', '\n\nEmergency generator shall:\n\n\uf0be\tmeet requirements for diesel engines given in 15', '\n\nEquipment required to secure a well in an emergency situation shall be defined for drilling and well intervention operations shall be minimum suitable for zone 2 or stricter in accordance with the area classification', '4) shall be suitable for operation in a hazardous area zone 2', '\n\nExhaust pipes from prime movers of emergency equipment shall neither emit sparks nor have a surface temperature which exceeds the ignition temperature of the gas mixture', ' Such equipment should be located in accommodation or in utility area close to the accommodation area in order to minimize gas exposure during an accidental event', '\n\uf0be\tShut-down of the emergency generator due to gas exposure, impose that all personnel onboard should prepare for evacuation in accordance with installation specific barrier strategy or emergency preparedness plan']
158 | 15.4.5 Hot surfaces | [' that can be exposed to leaks from flammable mediums shall not exceed minimum auto-ignition temperatures (AIT) for the hydrocarbon mixture in question', ' Insulating material shall, if applied, cover the entire hot surface', ' Necessary means of protection shall be provided to avoid that flammable medium can penetrate into the insulating material']
159 | 15.4.6 Static electricity | ['Objects that may collect an electric charge shall be connected to earth or bonded', '\n\nEquipment and material that may collect electric charge such as fibre-reinforced plastics shall conform to ISO 80079-36 or other relevant standard', '\n\nObjects shall be protected against electrical charges due to physical contact and then separation, or due to rapid flow of gases or liquids']
160 | 15.4.7 Cranes | ['1 and ventilation shall be disconnected / shutdown automatically upon single low gas alarm anywhere on the installation when crane is not in use', ' Dampers shall be closed when the ventilation is not running', '\n\nCranes located in non-hazardous areas shall as a minimum comply with the following:\n\n\uf0be\tExternal equipment shall be suitable for use in hazardous area zone 2', '\n\uf0be\tInternal/local equipment, if operative after crane shutdown and disconnection shall be suitable for use in hazardous area zone 2', '\n\uf0be\tDiesel powered cranes shall be fitted with flame arrestor in the combustion inlet', ' Spark arrestor shall be fitted in the exhaust outlet, but flame arrestor is not required', '\n\nWhen the crane is in use the following requirements shall be complied with:\n\n\uf0be\tUpon single gas alarm signal at any location on installation, the ventilation/dampers shall shutdown, and the crane operator shall immediately take the crane into a safe position, secure the load and initiate a manual shutdown that includes disconnection of ignition sources', ' Same actions shall apply on occurrence of an ESD situation', '\n\uf0be\tElectrical powered cranes shall upon confirmed gas detection in crane ventilation air intake initiate an automatic shutdown of crane (without time delay)', '\n\uf0be\tDiesel powered cranes shall on confirmed gas detection in either the neighbouring process areas of the crane or the ventilation or combustion air intake, initiate an automatic shutdown of crane (without time delay) in order to ensure an efficient disconnection of ignitions sources', '\n\nAdequate means for crane operator warning and consistent operating procedures shall be available']
161 | 15.4.8 Anchor handling equipment | ['Anchor handling winches should be located in non-hazardous area', ' A protection system to prevent sparks from anchor handling operations during an emergency situation to ignite a hydrocarbon release should be considered, e']
162 | 15.4.9 Temporary equipment | ['The platform shall be designed such that temporary equipment is shutdown according to the relevant ignition source groups and shall be performed by the platform ISC system as a minimum', ' All safety critical equipment and equipment in naturally ventilated areas shall be suitable for minimum zone 2', '\n\nFire and gas detection and other alarms related to temporary equipment shall be given to CCR', ' Relevant actions shall be initiated']
163 | 15.4.10 Ignition source control independence and reliability | ['ISC shall be independent of power distribution control system and PSD', ' If shunt trip principle is applied, a safety level similar to above shall be achieved considering design requirements such as dual control voltage, separate mini circuit breaker for shunt trip coil, redundant shunt trip coil and alarm on control voltage failure', '\n\nSwitching devices used to isolate electrical ignition sources shall be provided with a safety margin versus maximum design current in order to ensure adequate reliability and avoid malfunction', '\n\nThe breakers should be fail-safe', '\n\nThe electrical ignition sources, that are simultaneously isolated, should be fed by the same bus bar']
164 | 15.5 Survivability requirements | []
165 | 16 Human – machine interface (HMI) for CCR systems | []
166 | 16.1 Role | ['HMI in CCR shall provide system information presentation and means for operator interactions']
167 | 16.2 Interfaces | []
168 | 16.3 Required Utilities | []
169 | 16.4.1 General requirements for human-machine interface (HMI) | ['The HMI means shall include a main operating interface in CCR and in addition a CAP (a simplified safety matrix panel) allowing manual activation of critical safety functions', '\n\nThe HMI in CCR shall provide the means for operator awareness and actions and be suitable during emergency situations', '\n\nThe HMI shall be designed to prevent inadvertent operations due to operator misperception and unintended actions', '\n\nEN 62682 and EEMUA 191 should be used as basis for design of alarm functions']
170 | 16.4.2 Human-machine interface (HMI) status and alarm | ['The HMI facilities shall present system information in CCR such as:\n\n\uf0be\tESD hierarchy overview including status of ESD and EDP valves;\n\uf0be\tPSD hierarchy overview;\n\uf0be\tF&G overview, e', '\n\nThe CCR shall include VDUs with presentation of safety system information as its primary function', ' Number of VDUs shall depend on the result of the function and work task analysis', '\n\nThe HMI facilities shall include detailed safety system information such as input and output status, alarms, status of inhibit, override and suppression and system fault indication', '\n\nFailure to execute safety functions on demand shall initiate an alarm in CCR', ' Temporary equipment should be integrated within the CCR HMI']
171 | 16.4.3 Human-machine interface (HMI) control functions | ['The HMI facilities at CCR shall include the following safety control functions:\n \n\n\n\uf0be\tinitiate ESD level;\n\uf0be\tinitiate PSD level;\n\uf0be\tPSD level reset;\n\uf0be\tinhibit and override;\n\uf0be\tinitiate manual depressuring;\n\uf0be\tESD level reset;\n\uf0be\tF&G reset (e']
172 | 16.4.4 General requirements for critical action panel (CAP) | ['The Critical Action Panel (CAP) shall be independent of the visual display units and its associated data networks', '\n\nThe CAP shall encompass functions sufficient, in the absence of the main operator interface facilities, to bring the installation into a safe state']
173 | 16.4.5 Critical action panel (CAP) status and alarm | ['The CAP shall include the following status capabilities:\n\n\uf0be\tESD level activated;\n\uf0be\tstart of FW/foam pumps called for;\n\uf0be\tFW/foam pump running;\n\uf0be\tFW/foam ring main pressure;\n\uf0be\tactive fire protection release activation status;\n\uf0be\tactive inhibition/override – ESD;\n\uf0be\tactive inhibition/override - F&G', '\n\nThe CAP shall present the following alarms:\n\n\uf0be\tFW/foam pumps unavailable warning;\n\uf0be\tcommon fire alarm, (upon confirmed fire detection or release of fire protection means of the relevant area);\n\uf0be\tcommon manual call point alarm, (upon any manual call point of the relevant area in alarm state);\n\uf0be\tupon confirmed gas detection of the relevant area', ' When both flammable and toxic gas detection are provided, the alarm types shall be presented individually']
174 | 16.4.6 Critical action panel (CAP) control functions | ['The CAP shall include the following control functions:\n\n\uf0be\tmanual start of FW pumps;\n\uf0be\trelease of automatic firefighting systems;\n \n\n\n\uf0be\tactivation of ESD shutdown levels;\n\uf0be\tactivation of instant APS (ignition source isolation);\n\uf0be\tactivation of emergency depressurisation;\n\uf0be\tF&G common reset of inhibits and overrides;\n\uf0be\tESD common reset of inhibits and overrides']
175 | 16.5 Survivability requirements | []
176 | 17 Natural ventilation and heating, ventilation and air conditioning (HVAC) | []
177 | 17.1 Role | ['Natural ventilation shall\n\n\uf0be\tdilute gas concentrations and reduce the size of flammable gas clouds;\n\uf0be\tdilute harmful concentrations of smoke or toxic gases;\n\uf0be\tensure acceptable equipment environment', '\n\nHVAC shall, with respect to accidental events:\n\n\uf0be\tprovide pressurisation of rooms to prevent ingress of smoke or gas;\n\uf0be\tprovide smoke ventilation for internal fire conditions in low risk areas;\n\uf0be\tensure acceptable equipment environment;\n\uf0be\tdilute and remove concentrations of flammable gas, smoke and toxic gases']
178 | 17.2 Interfaces | []
179 | 17.3 Required utilities | ['HVAC system performance is dependent on\n\n\uf0be\temergency power supply to maintain ventilation should main electrical power supply fail;\n\uf0be\tinstrument air supply (local accumulators, if necessary)']
180 | 17.4 Functional requirements | []
181 | 17.4.1 Natural ventilation in hazardous areas | ['\n\nLocation and sizes for ventilation openings and louvers shall be optimised to maximize ventilation rates', ' Consideration shall in addition be made to maintain acceptable working environment /weather protection for personnel and equipment', '\n\nVentilation rates in hazardous areas shall as a minimum be 12 AC/h for 95 % of the time', '\n\nNatural ventilation shall be documented by studies and/or model testing', ' for noise suppression, shall be subject to special consideration', ' Stagnant zones should be avoided']
182 | 17.4.2 Mechanical ventilation in hazardous areas | ['A ventilation rate to ensure minimum 12 AC/h shall be provided', ' Ventilation shall be maintained in the event of a gas leak', '\n\nThe ventilation system shall ensure high availability, e', ' Alarm shall be given in CCR upon loss of ventilation in individual areas', '\nAdequate ventilation shall be monitored by fan operation or low air flow in the ventilation duct to the individual areas', ' Stagnant zones should be avoided', ' When calculating the gas release rate resulting from an oil leak, the evaporation effect should be taken into account, and not only the flash release']
183 | 17.4.3 Mechanical ventilation in non-hazardous areas with internal leakage sources | ['Ventilation shall be maintained in the event of an internal gas leak', ' To maintain non-hazardous status ventilation rates shall correspond to the relevant area classification calculations in areas with an internal leakage source, e', '\n\nThe ventilation system shall ensure high availability, e', '\n\nTurbine enclosures shall have a fixed over- or underpressure dependent on location (underpressure when located in an unclassified area and overpressure when located in a hazardous area)', '\n\nEquipment not suitable for zone 2 in areas with high ventilation shall automatically be disconnected upon loss of ventilation', '\n\nAlarm shall be given in CCR upon low air flow monitored by adequate fan operation or low air flow measured in main ventilation duct']
184 | 17.4.4 Mechanical ventilation in non-hazardous areas with “openings” towards hazardous area | ['There shall be a reliable overpressure (should be minimum 50 Pa) in non-hazardous rooms (safe by ventilation) with doors or openings giving direct access less than 3 m away from hazardous area', ' The self-closing door shall open into the non-hazardous room', '\n\nAlarm shall be given in CCR upon loss of ventilation', ' Alarm shall be given in CCR upon direct measurement of 25 Pa overpressure relative to surrounding classified areas', ' Alternatively, alarm shall be given both upon loss of airflow, corresponding to 25 Pa, and time delayed indication of open door', ' The flow or pressure differential signal shall be routed to the safety related part of SAS, initiating loss of ventilation alarm and if required activating automatic disconnection of ignition sources, see\nsubclause 15', '\n\nThe air change rate shall be minimum 5 AC/h with redundant fans', 'There shall be a reliable overpressure (should be minimum 50 Pa) in non-hazardous rooms (safe by ventilation) with doors or openings giving direct access less than 3 m away from hazardous area']
185 | 17.4.5 Mechanical ventilation in areas non-hazardous by location | ['There shall be a positive airflow into mechanical ventilated areas non-hazardous by location', '\n\nUpon loss of ventilation an alarm shall be given in CCR', ' The ventilation should be balanced to an equivalent overpressure of min 50 Pa']
186 | 17.4.6 Ventilation inlets and outlets | ['All ventilation inlets shall be located in non-hazardous areas, as far as practicable away from possible hydrocarbon leakage sources, and minimum 3 m from any zone 2 boundaries to reduce ignition probability', '\n\nEquipment in ventilation inlets and outlets shall be provided in accordance with clause 15 in order to ensure that such equipment does not become an ignition source during accidental events', ' Measures shall be taken, to avoid accumulation of ice and snow', '\n\nThe distance between air inlet and outlet from hazardous areas shall be such that:\n\n\uf0be\tGas from the outlet cannot enter the air inlet', '\n\nVentilation systems serving hazardous and non-hazardous areas shall be independent of each other', ' All ventilation outlets from non-hazardous areas shall be into non-hazardous areas', ' Studies should be made to locate main ventilation inlets to minimize exposure to smoke and gas leaks', '\n\nConsiderations should be made when locating LQ ventilation outlets to prevent exposure of helicopter deck from exhaust smoke during active smoke control', '\n\nThe inlet ducts should normally not pass through a hazardous area', ' Where this cannot be avoided, the supply fan unit should be located in the non-hazardous area (i', 'e at the inlet side) in order to secure that the pressure in the ducts supplying the room or equipment enclosure is higher than the external pressure, or adequate precautions should be taken to ensure that the ducts are free from leaks']
187 | 17.4.7 Dampers | ['Dampers shall provide quick, reliable and effective means to prevent ingress or spreading of gas or smoke', '\n\nA fire damper and smoke ventilation strategy shall be established for operation of dampers for both high and low risk areas, see NORSOK H-003', '\n\nGas tight dampers shall be installed in HVAC inlets and outlets', '\n\nIf gas and/or smoke are detected at ventilation air inlets, the ventilation fan in question shall be stopped, all inlet and outlet dampers shall be closed and the heating element shut off via F&G or ESD', '\n\nIn rooms where ignition sources are kept energised, hydrocarbon gas detection in the ventilation inlets shall ensure that a possible gas cloud is detected and dampers closed before a dangerous concentration can reach the ventilated areas', '\n\nThe total response time for closing of HVAC inlet dampers shall not exceed 6 s, i', '\n\nDampers and fans shall be interlocked to avoid abnormal pressure configurations', ' Ventilation (supply air and air outlet) shall continue upon internal fire in low risk areas', '\nFire-dampers shall be closed automatically by signal from the F&G-system and by “fusible link” where specified', ' Confirmed closed fire damper position shall be monitored from the CCR']
188 | 17.4.8 Survivability requirements | ['The system and components shall be designed and protected to ensure that it will remain operative during incidents where the system has a role or form a safety barrier', ' UPS, emergency communication rooms, CCR) shall be determined, including considerations of aspects such as temperature rise in case of HVAC trip', '\n\nHVAC system having a safety role shall be fed by emergency power to cater for loss of main power supply']
189 | 18 Public address (PA), alarm and emergency communication | []
190 | 18.1 Role | ['PAGA (Public Address & General Alarm system) Alarm and communication systems for use in emergency situations (until evacuation of the installation) shall:\n\n\uf0be\talert, inform and guide personnel as quickly as possible in the event of a hazardous or emergency situation;\n\uf0be\tprovide two-way communication of information regarding emergency events to the Control Room (CCR) or Emergency Control Centre (ECC);\n\uf0be\tprovide communication of requirements for emergency action to all personnel, and provide two- way communication between the emergency controller and the emergency response team;\n\uf0be\tallow the co-ordination of rescue, recovery and emergency assistance']
191 | 18.2 Interfaces | []
192 | 18.3 Required utilities | []
193 | 18.4.1 PAGA, loudspeakers, alarm horns/sirens, bells and alarm lights | ['Layout and location of loudspeakers, horns/ sirens and bells shall be reviewed during design and verified during start-up and operation', ' PAGA voice intelligibility levels shall be reviewed and verified', '\n\nAlarm voice communication shall be heard in a surrounding noise level up to and including 85 dBA', ' Flashing light shall be installed in areas with noise levels exceeding 85 dBA', ' In emergency stations, the\n \n\n\nalarm voice communication level shall be approximately 10 dB above normal surrounding noise level including noise from flare to avoid affecting speech communication for the emergency team', '\n\nThe system shall be designed to give appropriate access priorities']
194 | 18.4.2 Alarm signals | ['The alarm signals shall be in accordance with Table 4', '\nb\tPre-warning signal shall be used inside and at doors to rooms protected by gasses that could be lethal']
195 | 18.4.3 Internal emergency communication | ['The installation shall have necessary equipment for internal emergency communication so that emergency response teams can communicate with each other and with the CCR or the emergency preparedness management', '\n\nA telephone system shall be installed, so that personnel can alert the CCR', '\n\nCCR operators shall be able to communicate with operators anywhere on the installation', '\n\nTwo-way portable UHF radios shall be provided and used by the emergency response team', ' The system shall be able to handle emergency communication and the system shall be designed to give appropriate access priorities', '\n\nA “channel plan” and instructions/ practice for use of channels shall be established', '\n \n\n\nAt least two different communication facilities shall be available at the muster stations', ' The main facilities shall be hand portable radios and telephones', ' A microphone station to access PA system shall be located nearby the APS switch', '\n\nThe crane operator shall be able to communicate with the CCR, ships and operators on deck and have the sufficient equipment in crane cabin (e', '\n\nInstallation equipment for internal emergency communication shall be powered from dedicated battery supplies or powered from installation UPS system', '\n\nDrillers intercom function shall provide two-way communication in drilling areas between the driller and drilling personnel', '\n\nDrillers shall be able to communicate with the CCR according to emergency preparedness plans', ' The number and location of telephone should be limited to strategic locations considering, layout, MCP and radio communication']
196 | 18.4.4 External emergency communication | ['The installation shall have necessary equipment for communications with external emergency response resources', '\n\nThe communication systems shall allow communication with installations, helicopters, lifeboats, MOB boats, life rafts, vessels and shore', '\n\nEquipment for external communication shall be powered from dedicated battery supplies and/or powered from installation UPS system']
197 | 18.4.5 Telecommunication system in an emergency situation | ['Telecommunication systems required to remain active in an emergency situation shall not create additional hazards', '\n\nAntennas located within non-hazardous, naturally ventilated areas shall be provided in accordance with the following requirements;\n\n\uf0be\texplosion protection (electrical connections) suitable for use in zone 2, and\n\uf0be\t(1) the maximum transmission power is 6 W or less, or (2) the antenna is located in accordance with a safe distance requirement to avoid induction and sparks in adjacent structures, e']
198 | 18.4.6 Automatic personnel registration system | ['\n\nWhen used the automatic personnel registration system stations shall be installed at mustering stations, including mustering stations for emergency teams', ' It shall be possible to obtain personnel control by use of automatic personnel registration system in an emergency situation, also after activation of APS']
199 | 18.5 Survivability requirements | ['The central equipment room and batteries shall be located in accordance with requirements in 5', '\n\nThe PAGA system shall be divided into two independent systems (A system and B system) and power supplies for the respective systems should be installed in separate rooms', ' If the A and B systems are installed in the same room, necessary mitigations shall be implemented to minimize risk that a single incident affecting one system will have impact on both systems', '\n\nCabling of field equipment shall be routed such that the likelihood of damage due to external accidental loads and simultaneous loss of field equipment in several areas is minimized', ' Fire resistant cables shall be applied', '\n\nThe PAGA system shall be divided into two independent systems (A system and B system) and power supplies for the respective systems should be installed in separate rooms']
200 | 19 Emergency power and lighting | []
201 | 19.1 Role | []
202 | 19.2 Interfaces | []
203 | 19.3 Required utilities | ['Performance of systems for emergency power supply shall be independent on other utility system utilities']
204 | 19.4 Functional requirements | []
205 | 19.4.1 Emergency power supply | ['The emergency power supply shall consist of a combination of UPS and a diesel engine driven generator']
206 | 19.4.2 Uninterruptible power supply (UPS) | ['UPS shall have an operating capacity to supply the required emergency power to safety critical equipment as specified in accordance with the installation’s Safety Strategy', ' The available capacity shall, at any time when needed, ensure that safety systems will be kept operational during periods of accidental events, evacuation and escape', ' Power capacity shall be in accordance with ISO 13702 Table C', '\n\nShut down of ventilation in UPS room and/or emergency switchboard room shall not cause temperatures above vulnerable components’ tolerance within the required operating time of the relevant safety critical equipment', '\n\nIt shall be possible to isolate UPS for ignition source control', '\n\nThe UPS-system shall be monitored and raise critical status alarms in CCR']
207 | 19.4.3 Emergency power generator | ['The emergency power generator shall have a capacity of minimum 18 h at full load', '\n\nUpon zero voltage on the emergency switchboard, supply from the emergency power generator shall be established within 45 s', '\n\nThe transition from main power to emergency power shall not cause operational problems for the emergency power users', '\n\nEmergency power distribution shall be designed to allow maintenance and functional testing on the system without production shut down', '\n\nFor emergency generator(s) the following shall apply:\n\n\uf0be\tThe emergency generator system shall meet requirements stated in clause 15 Ignition Source Control such as flame arrestor in combustion inlet, and being tripped in accordance with requirements stated in subclause 15', '\n\uf0be\tIt shall be possible to isolate the fuel supply to each diesel driven generator from outside of the generator room', ' The valve shall be secured in open position', '\n\uf0be\tThe emergency generator system shall be self-contained', ' All necessary utilities shall fulfil the emergency system’s autonomy requirements and be available for a blackstart situation if required', ' Each system shall have a minimum capacity for six start attempts of minimum 5 s or longer if required by supplier', '\n\uf0be\tAir inlet shall be located such that exposure to possible gas leaks is minimized', ' The combustion air inlet shall be separated from the ventilation air inlet of the room in order to avoid vacuum in the room', '\n \n\n\nExhaust pipes from prime movers of emergency equipment shall with respect to ignition source control comply with clause 15', '\n\nThe emergency power system shall be monitored and raise critical status alarms in CCR', ' Equipment modus (emergency/ test) shall be displayed', ' Start of the emergency generator shall be possible from CCR', '\n\uf0be\tEach engine should have two independent starting systems, which do not need to be functionally different']
208 | 19.4.4 Emergency power consumers | ['It shall be identified which systems that are required to be operable during an emergency situation', ' These systems shall be supplied from emergency power', '\n\nThe emergency power shall be limited to supply of emergency power to equipment and systems having a function during an emergency situation', ' Typically, the following equipment shall have emergency power supply:\n\n\uf0be\tSAS;\n\uf0be\tHVAC system(s) for:\no\tareas containing group 3 equipment;\no\tmuster area(s);\no\tLQ in order to manage the emergency situation and normalization after an incident']
209 | 19.4.5 Emergency and escape lighting | ['\n\nThe operating capacity of escape lighting supply shall be sustained during the functional lifetime allowing a minimum of 60 minutes of illumination in accordance with EN1838, unless otherwise required in the Safety Strategy', '\n\nEmergency and escape lighting shall be provided in order to allow escape during emergency situations and provide sufficient lighting in areas which are manned during such events, e', '\n \n\n\nEscape lighting levels shall be minimum 15 lux at high risk task areas and at emergency, muster and embarkation areas and 1 lux on escape routes', '\n\nIn rooms which require manning in emergency situation the emergency lighting shall be defined through working environment studies', '\n\nEmergency exit signs shall either have an illuminated (local batteries only) or fluorescent type of design']
210 | 19.5 Survivability requirements | ['The emergency power systems shall be available outside initial accidental area located and/or protected against design accidental loads to ensure continuous operation', ' To achieve this emergency power and equipment rooms shall be located in accordance with requirements in 6', ' Emergency power generation shall be located in non-hazardous areas with a minimum exposure due to fire or explosion hazards', ' Emergency power switch boards and generator shall be separately located from main power', '\n\nThe UPS system shall consist of two independent systems (A and B) and located in dedicated rooms to increase robustness both with respect to possible electrical fires or gas ingress', '\n\nIf escape light fixtures without internal batteries are used, alternate fixtures shall be supplied from two different UPS systems and two well separated cable routes', ' The vulnerability of centralized UPS should be evaluated with respect to all faults and situations that can result in loss of all escape lighting, e']
211 | 20 Passive fire protection (PFP) | []
212 | 20.1 Role | ['Passive fire protection (PFP) shall ensure that relevant structures, piping and equipment components have adequate fire resistance with regard to load bearing properties, integrity and insulation properties during a design fire, and contribute in reducing the consequences in general']
213 | 20.2 Interfaces | []
214 | 20.3 Required utilities | []
215 | 20.4 Functional requirements | []
216 | 20.4.1 Fire divisions | ['Fire divisions shall as a minimum separate the main areas, unless it is proven that separation by distance is sufficient', ' However, well hatches shall be secured and withstand design explosion loads', '\n\nAreas with important safety functions and areas with a high fire risk shall be separated from the surroundings by adequate fire divisions', ' CCR, FW pump systems, LER/LIR with safety functions, emergency power supply with related distribution equipment and fuel tank shall be protected from the surroundings by minimum Class A-60 fire divisions', ' Cement units and associated equipment required for emergency operation (kill function) shall be protected from fire events to which they can be exposed', '\n\nFire divisions between fires areas exposed to HC fires shall remain intact with regard to the thermal loads and their duration to which they are subjected in the event of a design fire and shall be rated according to H-class', '\nFire divisions shall withstand the design accidental load', '\n\nGenerators (including prime mover), transformers, LER/LIR without safety function, rooms for ventilation equipment and equipment used for storage of flammable commodities or easily ignitable material shall be separated from the surroundings with at least Class A-0 fire divisions', ' for ventilation ducts, piping, drain boxes, cables, beams as well as windows and doors in fire divisions, shall not reduce the fire and explosion integrity of such divisions', ' Doors in fire divisions shall be of a self-closing type', ' It shall be documented that the high radiation load that may result from this is acceptable', ' This means that PFP on only one side shall be avoided if there is a fire risk from both sides', ' PFP on such divisions shall not be implemented without assessing the total risk impact', '\n\nThe extension of a fire division should be assessed with respect to exposure of personnel and critical equipment in neighbouring areas', ' Penetrations should be minimized in fire divisions between main areas']
217 | 20.4.2 Load bearing structures | ['Load bearing structures/important elements shall have adequate fire protection to prevent unacceptable deformations or collapse during a design fire, reference is made to subclause 7', '\n\nIf the contact area including the cross-sectional area inside hollow sections of an unprotected structural element is equal or larger than 1000 mm2, or for several attachments with at total contact area of\n1000 mm2 per square meter of fireproofed (main) structural elements, the need for coatback shall be evaluated', '\n\nFire protection materials used in outdoor areas should be suitable for the environmental conditions it may exposed to']
218 | 20.4.3 Vessels and piping | ['Pressurized vessels, process equipment and piping including supports shall have adequate fire resistance to prevent unacceptable ruptures (see subclause 5', ' For such equipment and piping consideration shall be given to deformations / movement of deck, walls and structural elements caused by explosion and fire loads', '\n\nPassive fire protection of process vessels and piping shall as far as possible be avoided, due to several negative aspects regarding safety such as corrosion problems, increased dimensions on equipment (increasing explosion pressures and drag loads) and maintenance issues', '\n\nThe bolts and nuts of flanges are weak points, and the need for passive fire protection on these to avoid unacceptable ruptures, shall be evaluated', ' The protection of these shall be kept as inspection and maintenance friendly as possible', '\n\nAnalysis of rupture of process equipment and objects when exposed to fire due to overpressure and material weakening should be performed as specified in “Guidelines for protection of pressurised systems exposed to fire”, Report 27', ' Bolts on flanges on liquid nozzles from large vessels, more than 4 tons of hydrocarbon liquid, should be protected']
219 | 20.4.4 Safety critical equipment | ['Equipment intended to function during a fire shall have adequate fire protection', '\n\nRequirements for fire protection and the use of PFP shall be assessed in relation to safety criticality and the fire risk in the area']
220 | 20.4.5 Non-combustible materials | ['Materials used in areas that may be exposed to a hydrocarbon fire shall be non-combustible', ' If it is justified from safety point of view to make use of materials that do not meet the requirements to non- combustibility, such materials shall have limited flame-spread properties, low smoke development, heat generation and toxicity of gas emitted in the event of a fire', ' Documentation shall be available to support the basis for the decision regarding selection of materials']
221 | 20.4.6 Living quarter and office/accommodation spaces | ['LQs with integrated offices etc shall be designed and protected to ensure that the safety critical functions can be maintained during design accidental events', '\n\nOuter surfaces of LQs and accommodation buildings shall be fitted with fire divisions of minimum A-60', '\n\nChoice of materials and interior design of the office/accommodation spaces shall be based on fire risk', ' If surface treatment of paint or other coating is used, the properties of the product with regard to flame- spread shall be considered', ' A corresponding evaluation shall also be carried out with regard to textiles', ' All materials shall have limited flame-spread properties, low smoke development, heat generation and toxicity of gas emitted in the event of a fire', ' Documentation shall be available to support the basis for the decision regarding selection of materials', '\n\nFire integrity of bulkheads and decks shall comply with clause 9 of the MODU Code', ' Where the MODU Code specifies steel bulkheads internally this shall be understood as A-0 divisions', ' pipes, tubing and cables shall be sealed with an approved fire protective method e']
222 | 20.5 Survivability requirements | ['The passive fire protection system shall resist the design accidental loads (explosion) to which they may be exposed', ' Jet fire resistance should be documented by testing in accordance with ISO 22899']
223 | 21 Active fire protection | []
224 | 21.1 Role | []
225 | 21.2 interfaces | []
226 | 21.3 Required utilities | []
227 | 21.4 Functional requirements | []
228 | 21.4.1 General | ['Fixed firefighting systems shall be installed in areas representing a major fire risk, and particularly cover equipment containing significant quantities of hydrocarbons or other flammable materials', '\n\nThe discharge effects from a fixed fire-fighting system shall be considered in selection of the system for particular areas (for example, the effects of water on electrical equipment)']
229 | 21.4.2 Fire water supply system | ['The fire water system capacity shall be sufficient at any time to cover the area with the largest FW demand plus the adjacent fire area with largest demand, plus two hydrants and, when applicable, fire water / emergency generator cooling', ' This capacity shall be achieved with one pump out of operation', ' Consideration shall also be made in the design for degradation of the pump performance to ensure sufficient pump system capacity at all times', '\n\nThe FW ring main shall be dimensioned for the demand of the largest fire area with one section of the ring main closed and for any FW pump configuration running, and for the demand of both the largest fire area and the largest neighbouring area without any sections closed off', '\n\nThe FW ring main shall be water filled and pressurised in the standby mode', ' The pressure source, typically a jockey pump, shall have the capacity of flow through frost protection bleed lines plus two hydrant hoses', '\n\nThe FW ring main sectioning valves shall be installed ensuring supply to consumers from two different sections allowing maintenance of the firefighting systems', ' The valves shall be easily accessible, car sealed open and clearly marked', '\n\nIf needed the FW ring main shall be equipped with two points (minimum 6 in) for connection to external water supply for commissioning', '\n\nThe magnitude and effects of pressure surges shall be minimised', ' Measures such as water filled FW pump risers, air relief valve and vacuum breakers shall be considered', '\n\nScreen at seawater inlet and strainer shall be installed upstream of ring main', ' The need for strainer between suction screen and pump shall be considered', ' The inlet arrangement shall be designed to ensure that the FW pumps also can function at 150 % of rated capacity', '\n\nThe system design shall comply with the field specific frost protection requirements, i', '\n\nCarbon steel and galvanised steel shall not be used in the FW ring main system', '\n\nThe water supply system and level control arrangement in water filled structures shall meet the required reliability', ' Consideration should be made to include capacity to helideck in order to meet the response time requirement, ref', ' SOLAS international shore couplings should be used']
230 | 21.4.3 Fire water pump arrangement | ['The basis for prime mover and FW pump system design shall be NFPA 20', ' Fire water driver/pump systems shall be self-contained and be used for fire water purpose only', ' It shall be possible to start the FW system even if no other systems on the platform are operational', '\n\nPumps powered through cable(s) from an external source shall be subject to special consideration for aspects such as reliability, configuration, ignition source control and survivability', '\n\nThere shall be a starting sequence logic for the start-up of the FW pumps in accordance with NFPA 20', ' There shall be a minimum of two pressure transmitters in the FW ring main providing the low-pressure start signal to the FW pump system', ' The transmitters shall be located in different sections of the ring main;\n\uf0be\tmanual start of FW pumps from CCR and FW pump room', '\n\nManual stop of the FW pump engines shall only be possible local to the engines', ' Each system shall have a minimum capacity for six start attempts of minimum 5 s or longer if required by supplier', '\n\nStart batteries for the FW pump engines and batteries for the diesel control system shall be located within the same room as the engines', ' The batteries shall be easily accessible and located above floor level', '\n\nA manual isolation switch/valve (car sealed) between the starter motor and the start battery/air bank shall be provided', '\n\nThe FW pump engine start batteries shall be charged by the FW engine generator while running and in addition charged from main power supply', '\n\nCompressed air accumulator capacity and/or battery capacity for FW pump engines shall be in accordance with NFPA 20', '\n\nThe fuel supply to fire water pump drivers shall be sufficient for a minimum of 18 hours operation at full load', '\n \n\n\nThe fuel supply shut off valve to the diesel engine shall be operable from outside the room', ' The valve shall be secured in open position', '\n\nThe FW pump engine cooling water and/or oil preheat function for diesel engines shall be in accordance with NFPA 20 requirements and supplier’s recommendations', '\n\nIt shall be possible to operate FW pump engines when ventilation to the room has been shut off', '\n\nIn case of gas detection in air inlet to the fire water pump engine room, the room ventilation shall be automatically shut down, dampers closed and the cooling air shall be taken from the engine room itself', ' Cooling of the fire water pump engine room shall be by an air/fire water-cooling unit powered directly from the fire water pump engine', ' The combustion air inlet shall be separated from the ventilation air inlet of the room', '\n\nThe combustion air inlet shall be equipped with a flame arrestor and an overspeed protection system', ' Automatic stop of FW pump engine driven FW pumps shall only be permitted due to overspeeding', '\n\nConsideration shall be made to 100-year wave condition to ensure sufficient pump suction pressure on pump duty point', '\n\nA test valve for the FW pumps shall be installed to enable checking of the FW pump curve up to 150 % of design flow rate', ' The valve shall be able to regulate from zero flow up to 150 % capacity and shall be of low noise design', ' It shall be possible to measure capacities and pressures', '\n\nIf the connection to CCR is lost, the fire-water pumps shall start automatically', '\n\nFire detection at the fire water pump shall not stop the pump or inhibit the start of the fire water pump driver', '\n\nEach engine should have two independent starting systems, which do not need to be functionally different']
231 | 21.4.4 Deluge system | ['There shall be a quick and reliable fire water supply to applicable deluge/water spray systems with a rate sufficient to cover the minimum demand for the applicable area and at pressures within the nozzle pressure range requirement', ' The deluge system shall provide adequate coverage for the relevant fire and explosion scenarios, with respect to both volume and area and equipment coverage', '\n\nThe FW system shall be designed and calibrated such that most remote deluge nozzles will receive water not later than 30 s after a confirmed fire signal has been given', '\n\nThe minimum required densities of FW shall be\n\n\uf0be\t10 (l/min)/m2 for process areas and equipment surfaces (including pumps and compressors)', '):\n \n\n\no\twith respect to tank decks on FPSOs, the application rate shall be minimum 6 l/min/m2 of foam solution', '\n\nThe deluge system piping and nozzle layout shall be such that it gives sufficient coverage (ref', ' Wind aspects shall be considered including nozzle location in deluge area periphery', '\n\nDeluge shall be automatically released upon confirmed gas detection in areas where effective for explosion mitigation', '\n\nIt shall be possible to manually activate deluge valve locally, from CCR and via push buttons located along the escape routes outside the fire area itself', '\n\nManual activation of deluge systems via pushbuttons shall trigger alarm in CCR, ESD2 and general alarm', ' Pressure transmitters fitted downstream deluge valves shall to provide confirmed flow signal to CCR, general alarm and initiate FW pump start', ', CCR, driller cabin) shall be considered in the design of the AFP system', '\n\nDeluge valve arrangement with interfaces shall be such that it can be function tested without release of water into the fire area, i', ' For elastomeric deluge valves a full capacity test line shall be included', ' Isolation valves shall also be included upstream of the deluge valve skids', ' Manual valves in deluge skid control circuits shall be secured in correct position e', '\n\nDeluge valves shall be provided with manual bypass including flow restriction to match flow through the valve', ' The deluge valve arrangement including bypass line shall be supplied from two different sections of the ring main ensuring FW supply also during maintenance situations', '\n\nDeluge valves shall fail in last position upon loss of signal from F&G logic which also provides deluge valve fault alarm in CCR', ' Upon loss of instrument air supply the deluge valve shall fail in open position', '\n\nFor manned installations resetting of deluge, monitor and sprinkler control valves shall normally only be possible local to the valves', '\n\nWhere applicable deluge valve stations shall have freeze protection systems according to project specifications', ' Piping downstream deluge and monitor skids shall be self-draining in accordance with Norwegian Oil and Gas Association GL075', '\n\nThe need for strainers in deluge system shall be considered', '\n\nCarbon steel and galvanised steel shall not be used in the deluge system', '\n\nNFPA 13, NFPA 15 and NFPA 16 should be used as guideline for design of deluge systems', ' All deluge valves covering a fire area should be released when fire is detected anywhere in the fire area', '\n\nFor other areas the protection should be in accordance the table in subclause 14', ' The application rates should be in accordance with ISO 13702 as relevant', ' High velocity deluge nozzles should be used for area coverage on fully open process and drilling areas as well as in areas where deluge is used for explosion suppression', '\n\nDeluge valves should be of a type which regulates the downstream pressure and which is not sensitive to pressure surges in the ring main', ' Deluge valve size should not exceed 10” in order to comply with response time requirement and avoid water hammer effects', ' Deluge nozzles should be without individual strainers']
232 | 21.4.5 Sprinkler system | ['The sprinkler system shall provide adequate coverage for the relevant fire scenarios, with respect to area coverage on horizontal and vertical surfaces', '\n\nAutomatic sprinkler systems shall be connected to a pressurized water supply so that the system is capable of immediate operation and no action by personnel is necessary', ' The sprinkler control valve shall be a quick opening type valve', '\n\nIt shall be possible to fully test the sprinkler system function by use of a suitably located test sprinkler and using fresh water', ' The connections shall be easy accessible from deck level and have a drain box located below the connection', ' Sprinkler valves arrangement shall be fitted with full capacity manual by- pass for the sprinkler valve to cater for sprinkler valve maintenance', '\n\nThere shall be a pressure sensor downstream of sprinkler valve which provides sprinkler release feedback to CCR', '\n\nCarbon steel and galvanised steel shall not be used in the sprinkler system', ' NFPA 13 should be used as guideline for design of sprinkler systems', ' The protection areas should be in accordance with the table in subclause 14', ' The application rates should be in accordance with ISO 13702 as relevant', ' There should be a test and flush connection at the far end of the piping system and at the sprinkler valve(s)']
233 | 21.4.6 Foam system | ['Foam supply shall be provided for all areas where hydrocarbon pool fires are likely to occur', ' The foam concentrate selected shall be suitable for use on the flammable liquids present in the area, in the expected environmental conditions and if appropriate through non-aspirating nozzles', ' Foam concentrate shall be compatible with sea water', ' The need for alcohol resistant foam protection shall be assessed in areas with large alcohol storage vessels', '\n\nFor deluge systems with foam additives, simultaneous activation of firefighting foam and water shall be automatic for confirmed fire detection', ' For release from CCR it shall be possible to select between water release only and water release together with firefighting foam', ' It shall be possible to stop the release of foam from CCR', '\n\nAll foam systems shall provide a quick and reliable supply of firefighting foams to applicable deluge and other water/foam based firefighting equipment with a rate and pressure sufficient to provide the correct foam concentration', '\n\nThe design of foam systems shall be based on recognized international standard, e', '\n\nFoam pumps shall be equipped with minimum flow control and pump testing facilities', '\n\nTo ensure positive injection of concentrates, the discharge pressure ratings of pumps at the design discharge capacity shall be in excess of the maximum water pressure available under any condition at the\n \n\n\npoint of concentration injection', ' The pressure in the foam concentration ring main shall be presented in CCR', ' A system shall be installed which is capable of providing sufficient foam system standby pressure', '\n\nFoam injector, ejector or proportioner shall provide a pre-determined foam concentration corresponding to the applied foam concentrate type', ' Foam shall be injected downstream deluge and monitor control valves to prevent ingress of foam into the FW ring main system', '\n\nBlock valves in the foam supply lines and foam ring main shall be secured open, e', '\n\nFor centralised foam systems, the total foam concentrate capacity shall be sufficient for minimum 30 min simultaneously supply to the largest fire area and the largest neighbouring area requiring foam', '\n\nFor local foam systems the total foam concentrate capacity in each local holding tank shall be sufficient for 30 min supply to the applicable deluge valve skid', '\n\nFoam release valves shall fail in last position upon loss of signal from F&G logic supplied with diagnostics alarm to CCR', '\n\nTo avoid foaming and contamination, it shall be possible to drain the foam concentrate tanks into transport tanks', ' If fire water is released upon confirmed gas detection, then foam should not be released', ' For manual activation of deluge from push button locally, the release of foam should be automatic', ' The foam pumps should be shutdown upon LALL in foam tank to prevent overheating']
234 | 21.4.7 Manual firefighting | []
235 | 21.4.7.1 General | ['Manual firefighting appliances, such as monitors, hydrants, hose reels, dry chemical equipment, dual agent hose reels and mobile and portable extinguishers shall provide a reliable and effective tool for firefighting by manual intervention', '\n\nThe facility shall be equipped with sufficient manual firefighting appliances to ensure effective firefighting of fires in the beginning stages and to prevent escalation', '\n\nWorking pressure and flow shall be in accordance with supplier’s equipment data sheet and equipment performance requirements and where applicable; in accordance with criteria for manual operation', '\n\nThe arrangement of the isolation valves shall be such that not more than 50 % of the water hoses and hydrants for one area is affected if one section of the fire water ring main is unavailable', '\n\nThe equipment shall have adequate frost protection in accordance with project specifications, e', '\n\nMonitors, hydrants, hose reels and dual agent hose reels intended for protection in one particular area shall not be fed from the same ring main section as for the deluge/sprinkler system for that same area', '\n\nIt shall be possible to reach any area where a fire may occur on the installation with at least two water jets from monitors or hose reels', '\n\nElectrical disconnection of equipment with voltage rating of 440V and higher in electrical equipment room shall be possible from outside the room, (e', ' Areas with deluge are excepted, but should have provisions for fire water either from hydrants or hose reels']
236 | 21.4.7.2 Hydrants and hose reels | ['The design of Standpipe and Hose System shall be based on recognized international standards e', '\n\nIn addition, the following shall apply:\n\n\uf0be\tThe maximum reaction force on the hose nozzle where only one person is supposed to operate the hose shall not be more than 250 N', ' Couplings shall be standard throughout the installation', ' Nozzles shall be of robust construction, easy to operate and made of materials suitable for the intended duty', '\n\nHydrants/hose reels shall be located in weather resistant cabinets', ' The cabinets shall be fitted with heating elements and should contain:\n\n\uf0be\t4 off 1½” fire hoses of an approved fire-resistant type, 15 m in length with instantaneous connection joints to hydrants and nozzles;\n\uf0be\ttwo water spray nozzles with pistol grip, with easy water pattern adjusts from straight stream to wide fog', '\n\nAll hydrants shall have two outlets fitted with 1½” quick connections of a standard approved type throughout all areas', ' should be stored adjacent to hydrants', ' The cabinets shall be fitted with heating elements and should contain:\n\n\uf0be\t4 off 1½” fire hoses of an approved fire-resistant type, 15 m in length with instantaneous connection joints to hydrants and nozzles;\n\uf0be\ttwo water spray nozzles with pistol grip, with easy water pattern adjusts from straight stream to wide fog', '\n\nNon-collapsible hose reels should have 25 m hose']
237 | 21.4.8 Monitors | ['Activation of a fire monitor shall be from a location at sufficient distance protected from the fire', ' CCTV coverage for remote operation shall be considered', '\n\nArrangement of monitors which can be remotely actuated, shall be selected to minimise risk of personnel injury', ' Local manual override controls shall be provided', '\n\nMonitors shall have sufficient freedom of travel in the horizontal and the vertical plane to be able to cover the specified area during specified wind conditions', ' It shall be possible to lock the monitor in any position', ' Automatic monitor valves shall fail in last position upon loss of signal from F&G logic and/or signal from remote control panel', '\n\nMonitor nozzles shall be of the constant flow type, i', ' the flow shall be the same at both fog and at jet spray setting', ' The spray angle shall be easily adjusted when in operation and return to maximum spray angle after use', '\n\nWhen monitors are used instead of deluge systems the requirements for deluge systems shall apply', ' Where there are dry pipe sections between the monitor and the monitor valve, the possibility for detrimental pressure peaks (water hammering) shall be considered', '\n\nAuto drain valve facilities shall be provided for each fire water monitor', '\n \n\n\nAreas with well intervention shall be covered by fire water monitors', ' At least 2 monitors shall be available to account for high wind', ' The release function shall be located along escape ways from the area protected from the fire', '\n\nIt should be possible to operate remote controlled monitors both from central control room and from a local control panel at a sufficient distance from the fire']
238 | 21.4.9 Helideck firefighting system | ['The helicopter deck shall be equipped with adequate fire protection equipment and with sufficient drainage capacity to enable escape and firefighting in the event of helideck related fires', ' This shall be achieved by complying with the following sub-requirements:\n\n\uf0be\ta DIFFS shall be the preferred means of active fire protection and shall comply with:\no\tthe water-foam mix shall be applied with a minimum spray height corresponding to the top of the applicable helicopter bodies in calm conditions', ' This to ensure a safety margin with respect to safe escape, including windy conditions;\no\tthe water density shall be minimum 10 (l/min)/m2 for the helideck;\no\tfull water and foam supply shall be available within 20 s from time of activation;\no\tthe storage capacity of the foam concentrate holding tanks shall be sufficient for 10 min of full discharge of the DIFFS;\no\tactivation and deactivation shall be from both local and remote protected position', '\n\uf0be\tfoam monitors (not required when DIFFS is installed) shall, when installed, comply with:\no\tone monitor to be located at each of the three access ways;\no\tthe foam monitor firefighting system shall be capable of delivering foam on the helicopter deck maximum 20 s after activation at a rate of minimum 1 500 l/min per monitor at\n0,7 MPa (7 barg) nozzle pressure;\no\tfoam monitors shall always start automatically with water spray in the fog position;\no\tit shall be possible to start, stop and control monitors from both local and remote protected position;\no\tthe storage capacity of the foam concentrate holding tanks shall be sufficient for 10 min of full discharge;\no\trisk assessment justifying the use of monitors as an alternative to DIFFS', '\n\uf0be\tthe equipment shall have adequate frost protection, i', ' by heat tracing and/or drain;\n\uf0be\ton NNMI the firefighting system on helideck, if installed, shall allow for remote operation and control;\n\uf0be\tFW and spilled fuel shall be drained in a safe and controlled manner through a dedicated drain system with sufficient capacity', ' Special attention to location of drain gullies shall be made to helicopter decks on floating installations;\n\uf0be\tthree dual agent hose reels (combined water/foam and dry chemical hose reel) shall be provided at the stairways and have:\no\tsufficient powder for discharge at a rate of 2 kg/s to 3 kg/s for minimum 100 s;\no\tsufficient foam for minimum 10 min full discharge']
239 | 21.4.10 Extinguishing systems in enclosed compartments | []
240 | 21.4.10.1 General | []
241 | 21.4.10.2 Water mist system | ['The water mist systems shall provide a quick and reliable discharge of water mist at a sufficient density and at sufficient duration for adequate fire suppression and control', ' Selection of type of water mist system (local and/or full flooding) shall be based on fire scenario, and described in safety strategy', '\n\nWater mist systems shall also comply with the following requirements:\n\n\uf0be\teasily accessible manual release facilities shall be provided at each entrance to the protected areas;\n\uf0be\tthe ventilation (fans and/or dampers) shall be closed and the equipment shut down before release of water mist systems;\n\uf0be\tthe water mist cabinet shall be located outside of the protected room;\n\uf0be\tthe water mist skid including compressed gas bottles shall be certified for the actual maximum operating pressure;\n\uf0be\tcompatible materials shall be used throughout the system, e', '\n\nThe water mist system shall have an external connection to have the possibility to use fire water after the fresh water tank and the nitrogen tank are emptied', ' NFPA 750 should be used as guideline for design of water mist systems', '\n\nWater quantities and release duration should typically be determined taking into consideration the size of the area and the degree of congestion, the fuel type and the nature of the fires which may be experienced, equipment types within area (e', ' Release duration and design should be in accordance with contractor’s recommendations, and/or typically range from 5 up to 30 minutes as indicated in NFPA 750 depending on application']
242 | 21.4.10.3 Gaseous agents | ['The gaseous firefighting system shall provide a quick and reliable discharge of gaseous agents for fire mitigation at sufficient concentration and at sufficient duration for adequate fire suppression and control, in addition retaining an atmosphere non-harmful to humans', '\n\nGaseous firefighting systems shall also comply with the following requirements:\n\n\uf0be\tprotection by use of CO2 or other noxious and poisonous gases shall not be used;\n\uf0be\tin order to enable personnel to evacuate before gas discharge, appropriate means for warning of gas release prior to release shall be provided, i', ' clearly visual and audible alarms;\n\uf0be\tall rooms protected by gaseous agents shall be furnished with clear audible and visual means for system status annunciation on the outside at the room entries;\n\uf0be\tthe room where the gaseous agent is released shall be sufficiently tight to maintain the prescribed concentration for the pre-determined time period of minimum 10 min;\n\uf0be\tthe ventilation (fans and/or dampers) shall be closed and the area isolated before release of gaseous systems;\n\uf0be\tthe compressed gas bottles shall be certified for the actual maximum operating pressure;\n\uf0be\tthe gas bottles shall be located outside of the protected room;\n\uf0be\twhere appropriate, the system shall be monitored to enable the detection of faults which may affect the operational efficiency of the system;\n\uf0be\teasily accessible manual release facilities shall be provided at the entrances to the area;\n\uf0be\tisolation of power to electrical equipment to be considered']
243 | 21.5 Survivability requirements | ['System and components incorporated shall resist design accidental loads to which they may be exposed', '\nThe FW ring main shall be routed outside areas where it could be exposed to damage, and be protected against external forces, such as environment, falling loads, fire and explosion', '\nThe fire water and centralised foam pumps, drivers (including electrical supply from dedicated generators and other sources) and controllers shall be located in the accommodation or utility area', '\n\nFire pump arrangements shall be independent of each other', '\n\nThe FW and centralized foam pump systems shall be connected to the ring main at different locations to avoid loss of FW supply', '\n\nCables for fire water and centralized foam pumps shall be fire resistant in accordance with IEC 60331', '\n\nSolutions with centralized deluge skids (multi deluge valve skids) shall be located in the accommodation or utility area well protected from hydrocarbon related accidental events', ' Supply lines from the deluge valve to the fire area they protect shall be routed such that exposure to accidental loads are minimized', ' The dry supply lines including pipe supports shall be provided with sufficient passive fire protection to ensure that they can fulfil their role', ' The supply lines shall also withstand the design explosion loads in relevant fire areas', '\n\nControl valves for sprinkler and deluge systems shall be located outside the area they protect and they shall be protected against design fire- and explosion loads', '\n\nDamage in one area shall not cause loss of fire water supply to other areas', ' Special consideration should be given to protection of non-metallic materials and soldered joints', ' The need for additional protection and cable routing should be evaluated', ' Penetrations through fire partitions should be avoided', '\n\nIf more than one deluge valve is required to cover a fire area, separation of the supply lines and interlacing of deluge nozzles (fork shaped pattern) to improve robustness should be considered']
244 | 22 Escape and Evacuation | []
245 | 22.1 Role | []
246 | 22.1.1 Escape routes and exits | []
247 | 22.1.2 Mustering areas | []
248 | 22.1.3 Evacuation systems | []
249 | 22.2 Interfaces | []
250 | 22.3 Required utilities | []
251 | 22.4 Functional requirements | []
252 | 22.4.1 Escape routes and exits | ['Escape routes shall be provided enabling all personnel to safely leave the affected area(s) in case of a hazardous incident', '\n\nEscape routes shall by default be part of the daily used transport- and passageways', '\n\nAll doors shall be constructed so that one person can easily open them from either side', ' They shall open in the direction of escape without blocking the outside route, and be self-closing', '\n\nRequired width of escape routes shall allow easy transport of injured personnel on a stretcher', ' The dimensions shall minimum be 1 m in width (0,9 m for doors) and 2,3 m in height (2050 mm for doors)', ' It shall be demonstrated in all cases that equipment used for transportation of injured personnel can be turned at corners and in the stair cases', '\n \n\n\nEscape routes intended for use by more than 50 persons shall be 1,5 m (1,2 m for doors) in width', ' Floor slope in escape shall not exceed 10 %', ' Single steps in escape routes shall be avoided', '\n\nLifts shall not be considered as a part of escape routes', ' However, it shall be possible to escape from the lift and the hoist way with the lift at any elevation', ' Lift shall automatically go to next floor level and stop upon fire alarm and gas alarm', ' Escape from legs/shafts/columns of an installation shall be considered separately, and if use of lift is necessary to ensure adequate and effective escape, the lift system shall satisfy special requirements, e', ' This requirement should consider the effect of wind (1 year condition), list (typically 17° for floating installations) and snow/ice conditions', ' due to two separate incidents, a sliding door should be used']
253 | 22.4.1.1 Outside buildings | [' There shall be at least two exits to escape routes from permanently or intermittently manned areas leading in different escape directions and situated as far apart from each other as possible', '\n\nFor intermittently and permanently manned areas, there shall be at least two access ways to escape routes', '\n\nEscape routes on decks shall be provided with a non-skid, oil resistant coating in yellow', ' On deck grating, two parallel 100 mm wide yellow lines shall be painted indicating the width of the escape route', ' The number of these stairways shall be assessed based on the platform size, configuration of areas and equipment layout', '\n\nEscape routes shall be arranged from the drill floor to adjacent modules and also down the substructure', ' It shall be possible to escape from a drilling area without running through a wellhead area', 'Escape elsewhere than in the LQs and offices should preferably be provided on the outside along the periphery of the installation, and be designed to be passable by position rather than by special protection', '\n\nEscape routes leading to a higher or lower level should be provided by stairways', ' Protection of these escape routes from radiation heat should be considered', '\n\nFor derricks, an escape arrangement leading away from the derrick to a safe area should be considered in addition to the main access routes']
254 | 22.4.1.2 Inside buildings | ['There shall be at least two exits for areas where more than 15 persons may assemble such as offices and rooms in LQs exceeding 20 m2', ' In addition, at least one of the two routes leading in different directions from each level in the LQ shall be an internal stairway linking all levels', ' Internal room arrangement shall be considered for possible blocking of exits following an accident, e', '\n\nCorridors in permanently or intermittently manned areas shall not exceed 5 meters, unless provided with at least two exits, one at each end']
255 | 22.4.1.3 Signs and markings | ['A sufficient number of safety signs and markings shall be provided to convey necessary information to guide personnel in emergency situations and give clear information regarding directions/locations of various functions, areas and exits', '\n\nSafety signs and markings shall conform with NORSOK C-002 and shall be consistent throughout the installation, and the colour code used shall be specific and not used for other purposes', ' A descriptive text,\n \n\n\nin Norwegian and in English, shall be included if the symbols are not easily understood', ' Text shall however be kept to a minimum', '\n\nEscape routes inside offices and living quarters shall be provided with directional guidance showing correct escape direction in accordance with ISO 16069 Safety Way Guidance System (SWGS)', '\n\nSafety plot plans shall be strategically located / posted on the premises with high degree of accessibility and shall include:\n\n\uf0be\tlocations of safety, rescue and firefighting equipment;\n\uf0be\temergency exits and escape routes;\n\uf0be\tevacuation instructions and legends', ' Other enclosed and regularly manned utility and process areas should be considered separately']
256 | 22.4.2 Evacuation systems | []
257 | 22.4.2.1 General principles | ['Requirements relating to safe evacuation shall be met by using a combination of means of evacuation', '\n\nNumber, size and location of evacuation means shall be established based on manning, risk analyses (e', '\n\nThere shall be sufficient emergency lighting of the sea surface to ensure safe launching of evacuation means in darkness, ref', '\n\nThe preferred methods of evacuation for installations that are not bridge connected to a neighbouring installation are in prioritised order:\n\n1)\tHelicopter (if possible in an accidental scenario)\n2)\tFree-fall lifeboats\n3)\tEscape chute with life rafts\n\nFor installations connected by bridge to other installations and/or floating accommodation installations that are safe in the design accidental event, the bridge should be the primary means of evacuation']
258 | 22.4.2.2 Lifeboats | ['The minimum number of free-fall lifeboats in the main evacuation area available during a design accidental event shall correspond to the maximum number of personnel (100 %) on board plus one additional boat to compensate for unavailability (technical failure when required)', ' The maximum number of personnel on board shall include day visitors and shuttle personnel in transit (waiting for helicopter in sky lobby), but excluding crew change when helicopter is on deck', ' For floating installations, it shall be possible to launch lifeboats with capacity for all persons on board at the least favourable angle of heel specified in the stability calculations combined with weather condition with one year return period', '\n\nFree fall lifeboats shall comply with DNVGL-ST-E406: Design of Free Fall Lifeboats', '\n\nAll free-fall lifeboats shall be launched as part of commissioning using design drop height, angle and weight', ' The distance between lifeboats and platform structure shall be large enough to ensure a safe drop of the lifeboats, ref', '\n\nFor NNMI, simpler evacuation means may be acceptable and shall be evaluated and described in the safety strategy', ' The disconnection point should be in the vicinity of the lifeboat and disconnection shall be automatic without sparks when dropping or lowering the lifeboat;\n\uf0be\tdisconnection and launching mechanism should be considered to be winterised to prevent ice from interfering with the launching;\n\uf0be\twinch for recovery of lifeboat from sea should be fed by main power;\n\uf0be\taccess ways should be provided with anti-skid coating;\n\uf0be\tshall be equipped with:\no\tlifeboat navigation assistance system (LNA), i', '\n \n\n\nThe distance between lifeboats and escape chute should be optimised to ensure that a dropped boat will not hit a lowered escape chute and boarding platform during relevant weather conditions', '\n\nThe lifeboats:\n\n\uf0be\tshould have emergency power for power supply to lifeboats', ' The disconnection point should be in the vicinity of the lifeboat and disconnection shall be automatic without sparks when dropping or lowering the lifeboat;\n\uf0be\tdisconnection and launching mechanism should be considered to be winterised to prevent ice from interfering with the launching;\n\uf0be\twinch for recovery of lifeboat from sea should be fed by main power;\n\uf0be\taccess ways should be provided with anti-skid coating;\n\uf0be\tshall be equipped with:\no\tlifeboat navigation assistance system (LNA), i']
259 | 22.4.2.3 Escape chutes: | ['In the vicinity of the muster area at least one escape chute with minimum capacity of the largest lifeboat shall be included', ' The life rafts and boarding rafts shall be lowered together with the chute and the boarding raft shall automatically inflate', ' Escape chute and rafts shall be type approved and tested according to SOLAS and national maritime regulatory requirements', ' With respect to life raft capacity, a personnel weight of 100kg including survival suit shall be used (similar as for lifeboats DNVGL-ST-E406)', '\n\nThe following apply for escape chutes:\n\n\uf0be\tthey shall be readily available and easy to operate with clear operating instructions located on the wall inside the container;\n\uf0be\tthe winch for recovery should be fed by main power;\n\uf0be\tremoval of life rafts for re-certification shall be possible without affecting the suspension system including lifting wire;\n\uf0be\tportable AIS-SART and VHF radios to be located at each escape chute station', '\n\nThe following apply for escape chutes:\n\n\uf0be\tthey shall be readily available and easy to operate with clear operating instructions located on the wall inside the container;\n\uf0be\tthe winch for recovery should be fed by main power;\n\uf0be\tremoval of life rafts for re-certification shall be possible without affecting the suspension system including lifting wire;\n\uf0be\tportable AIS-SART and VHF radios to be located at each escape chute station']
260 | 22.4.3 Survival suits | [' Survival suits shall be based on Norwegian Oil and Gas Association GL094 “Kravspesifikasjoner for redningsdrakt til bruk på norsk kontinentalsokkel”, with the exception of the requirement of turning unconscious personnel', 'Survival suits for 75 % of maximum POB should be available at the main mustering area', ' If alternative lifeboat or escape chute stations are provided, survival suits should be available in accordance with the evacuation means capacity/study']
261 | 22.4.4 Muster area | ['The muster area(s) shall be located outdoors by a primary or secondary embarkation area (preferably both), or in a protected area with easy access to the embarkation area(s)', ' The muster area(s), and the route(s) from the muster area(s) to the embarkation area(s) in question, shall be arranged and protected in order to ensure the safety of all personnel during the period required for the evacuation process to be completed in an organised and efficient way', '\n\nThe size of the muster area shall minimum correspond to N*0,4 m2, where N denotes maximum POB', ' The size of mustering area for alternative lifeboat and escape chute stations shall be 0,4 m2 per person', ' Consideration should be made to periods with higher manning such as maintenance shutdowns where additional lifeboat is utilized']
262 | 22.5 Survivability requirements | []
263 | 22.5.1 Eurvivability of escape routes | ['Escape routes outside the area for the initial event shall minimum be designed and protected so that at least one route of escape is available for the required period of time (reach mustering area) during a design accidental event, including possible search and rescue operations if defined in safety strategy', ' Personnel shall be able to use the escape routes without being exposed to excessive toxic fumes, smoke nor unacceptable heat loads', ' Where this is not possible, external escape routes shall be physically separated from open hazardous areas by blast- proof and fire-proof walls, or alternative routes shall be provided which are unlikely to be affected by the same incident', '\n\nComposite grating shall not be used in escape routes if they can be exposed to hydrocarbon fires', '\n\nEscape routes should be designed to remain passable by location rather than by protection', '\n\nSteel should be used in escape routes that may be exposed to hydrocarbon fires including handrails and stairs']
264 | 22.5.2 Survivability of evacuation means and muster area | ['Muster area and evacuation means shall minimum be designed and protected for the period of time required to ensure safe muster, search and rescue operations if defined in safety strategy, embarkation and abandonment of the installation during a design accidental event', ' Consideration should be made to include smoke protected entrance from muster area to the lifeboats']
265 | 23 Rescue and safety equipment | []
266 | 23.1 Role | []
267 | 23.2 Interfaces | []
268 | 23.3 Required utilities | []
269 | 23.4 Functional requirements | []
270 | 23.4.1 Man over board (MOB) boat | ['The facility or standby vessel shall have a MOB boat available at all times', ' when working over sea or helicopter traffic relying on MOB boat recovery, two independent MOB boats shall be available', '\n\nThe MOB boat and launching arrangement, including loose equipment, shall as a minimum be in accordance with the IMO LSA Code (SOLAS) and NMA regulation no 90', '\n\nIf a crane is used for launching, the following requirements shall apply:\n\n\uf0be\tThe crane and the MOB boat shall be designed for the application', '\n\uf0be\tThe MOB boat shall be visible from the crane cabin during handling', '\n\uf0be\tThe MOB boat shall have a fixed lifting frame with one-point suspension for handling by cranes', '\n\nThe availability of the MOB system(s) shall ensure compliance with defined time requirements for recovery of personnel from sea, ref', '\n\nMan-overboard boat crew shall have dedicated personal equipment such as suits etc', ' In addition to the suit shall clothing adapted to the climatic conditions be available', '\nEquipment kept in the man-overboard boat shall be properly stored', ' It should be possible to launch and recover the MOB boat in 6 m significant wave height, reference NORSOK R-002 Lifting Equipment', '\n\nOne watertight cabinet for storage of gear for the MOB boat crew should be installed in the vicinity of the MOB boat', ' The content of the cabinet should include:\n\n\uf0be\t4 swimsuits of wet suit type;\n\uf0be\t6 survival suits (to be compatible with possible use of helmets);\n\uf0be\t1 thermal protection blanket;\n\uf0be\t1 VHF radio with suitable charger;\n\uf0be\t3 life jackets;\n\uf0be\t30 m lifeline;\n\uf0be\ta pair of flippers;\n\uf0be\ta diving knife;\n\uf0be\ta diving mask with breathing tube;\n\uf0be\ta dive torch;\n\uf0be\ta boat hook (telescope);\n\uf0be\ta sea anchor;\n\uf0be\ta tow rope with hook;\n\uf0be\tsuitable equipment to ensure proper pickup of personnel from the sea, e']
271 | 23.4.2 Safety showers and eyebaths | ['Areas where chemical or hot fluid spillage may occur exposing personnel shall be identified', '\n\nAdequate fresh water quality shall be used for safety showers and eyebaths']
272 | 23.4.3 Safety station cabinets | ['An adequate number of safety station cabinets shall be provided', ' The cabinets shall be painted green (RAL 6002)', ' They should contain\n\n\uf0be\tfour vacuum wrapped blankets;\n\uf0be\tone scoop type stretcher;\n\uf0be\tone basket type stretcher;\n\uf0be\tone first aid kit;\n\nor as otherwise required in the EER analysis']
273 | 23.4.4 First aid kits | ['An adequate number of first aid kits shall be provided at suitable locations, e']
274 | 23.4.5 Lifebuoys | ['Lifebuoys shall be located at regular intervals along the periphery of the lower levels of the installation, according to MODU Code 10', ' Lifebouys with smoke signals shall be limited in numbers and placed in non-hazardous areas']
275 | 23.4.6 Firemen’s equipment | [' The number of sets of firemen’s equipment required and the contents of each set shall be assessed', ' Breathing air bottles shall be of composite material type', "Firemen's equipment should be stored in sets at no less than two locations separated from each other, so that access to all equipment will not be blocked in the event of a fire in one area", '\n\nInstallations should have dedicated equipment for refilling breathing apparatus']
276 | 23.4.7 Smoke hoods/breathing masks | ['Breathing masks and/or smoke hoods shall be installed as follows:\n\n\uf0be\tone smoke hood per bed in LQ cabins;\n\uf0be\tbreathing masks and/or smoke hoods for escape from / through indoor and outdoor areas exposed to toxic fumes or smoke shall be considered and strategically located, e', ' crane cabin;\n\nThe equipment shall be in accordance with EN 403 or similar']
277 | 23.5 Survivability requirements | []
278 | 24 Marine systems and position keeping | []
279 | 24.1 Role | [' The roles of the various systems are as follows:\n\n\uf0be\tthe ballast system shall provide easy and reliable facilities for ballast water distribution in order to maintain control of the floating offshore installation during routine operations and emergency situations, in terms of stability, heel, trim and draft and ensuring that hull stresses do not exceed the design strength criteria;\n\uf0be\tthe bilge system shall provide easy and reliable facilities for pumping from and draining of watertight compartments;\n\uf0be\tthe weight and stability monitoring systems shall ensure that weights do not exceed the structural capacity and that weight distribution is such that stability curves are not exceeded;\n\uf0be\tthe weather- and watertight closing means such as doors and hatches shall maintain the watertight divisions during all operating conditions;\n\uf0be\tthe position keeping system shall enable the floating installation to maintain position and heading within given operational limits']
280 | 24.2 Interfaces | []
281 | 24.3 Required utilities | ['The marine systems performance is dependent on:\n\n\uf0be\temergency power supply to keep ballasting systems operational and maintain position keeping should main electrical power supply fails;\n\uf0be\tcargo handling system including LCS;\n\uf0be\ttelecommunications for positioning']
282 | 24.4. Functional requirements | []
283 | 24.4.4.1 Ballast and bilge system | ['The ballast system shall ensure that hull structural loads are maintained within the design strength limits', ' The bilge system shall be an effective means for draining watertight compartments', '\n\nThe ballast and bilge system shall comply with the requirements in\n\n\uf0be\tNMA Regulations No', ' The ballast pumps shall have capacity to maintain the operational draft during loading/offloading operations', '\n\nAll ballast tanks shall be provided with two independent level measuring systems based on different measuring principles, one of the two remotely', ' For ballast tanks which are not always accessible for checking of tank level, two independent remote systems shall be arranged', '\n\nBallast system valves shall be designed fail-to-close', ' The ballast valves position shall be indicated in marine CCR', ' Hand pumps for operation of ballast tank valves and solenoid valves shall be available in case of failure in the ballast control system', '\n\nFor ship shaped structures where ballast pumps are located in the cargo pump room, all ignition sources shall be located in a separate safe area', ' Electrical motors shall not be located in the cargo pump room itself', '\n\nFor column-stabilized units, the ballast sea water shall not be routed in or out directly from sea but via a point above the waterline in damaged condition', '\n\nThe ballast system shall be arranged so as to prevent any single failure in the system or any operator failure from causing ballast water to be inadvertently transferred from one tank to another or causing the unintentional flooding or emptying of ballast tanks', '\n\nThe ballast system shall be provided with power from the emergency switchboard', ' The bilge system shall be an effective means for draining watertight compartments', '\n \n\n\nThe ballast control system shall incorporate an emergency stop device on the ballast control console, which can isolate or disconnect the power supply to the remote-control system and to the pumps', ' The ballast system shall then automatically change to safe position, i', '\n\nBallast system should be arranged with cross connections ensuring that ballast water can be cross fed from one side of the vessel to the other as a contingency measure']
284 | 24.4.2 Water- and weathertight Integrity | ['Void spaces which are regarded as buoyancy volumes shall be provided with means for checking water tightness, e', '\n\nWatertight structural members such as box-beams shall be provided with means for effective drainage and sounding, e', '\n\nWatertight closing means shall be arranged for all openings and penetrations through watertight bulkheads and decks in order to maintain the unit’s watertight divisions', '\n\nWatertight closing appliances shall be provided in all openings in hull and superstructure ensuring watertight integrity as indicated by the freeboard plan', '\n\nWatertight closing appliances shall be capable of being opened and closed locally from both sides of the door mechanically or hydraulically and by means of a hand pump', '\n\nThe control system for watertight closing appliances shall provide the necessary alarms and visual indication in the control room with respect to open and closed status of the closing appliance', '\n\nWatertight doors shall be designed so that personnel cannot be injured by the door, (crushing), during normal operation', ' The doors shall not close automatically during normal operation', '\n\nWeathertight closing means shall be kept closed', ' Instructions to this effect shall be posted on the closing means']
285 | 24.4.3 Weight and stability control | ['Weights shall be monitored and controlled to ensure compliance with structural design criteria and stability curves', ' modifications shall be assessed against the platform structural design capacity and stability curves', '\n\nAll permanent changes in weight and distribution of weight shall be recorded in a systematic manner, e', '\n\nTemporary changes in weight shall be in accordance with the allowable loading limits specified', '\nA weight control procedure shall be available, and shall clearly identify the procedure to be followed and the roles and responsibilities of the key personnel involved, when recording permanent and temporary weight changes on the platform', '\n\nAn updated stability analysis model shall be available', '\n \n\n\nThe lightweight condition and centre of gravity for the installation in the various operating conditions shall be followed up, e', '\n\nAudible alarms shall be initiated upon filling/emptying of ballast or cargo tanks outside limits approved in the LCS', ' Consideration should be made to weight or stability changes due to release of fire water']
286 | 24.4.4 Position keeping system | []
287 | 24.4.4.1 General | ['The position mooring system shall maintain the unit on location and if applicable enable relocation of the unit', ' Heading control shall be kept within defined design limits', '\n\nIn addition, the need for quick re-positioning of the installation in case of specific emergency situations shall be evaluated', '\n\nThere shall at all times be an updated mooring analysis which reflects all applicable operating scenarios (ultimate limit state (ULS), accidental limit state (ALS) and fatigue limit state (FLS)) and shall be verified in accordance with latest regulatory requirements, e', '\n\nThe positioning mooring system shall be capable of providing sufficient capacity to satisfy the positioning holding required in the mooring analysis', '\n\nDue to poor fatigue qualities, connection elements such as kenter shackles, pear links, C-links, D-shackles with locking pin through bow, pins and swivels shall not be used in permanent mooring systems', '\n\nA system for continuous measuring of anchor line tension, which monitors anchor line tension and compares with high and low values shall be provided', ' The system shall be calibrated regularly and it shall be ensured that line tension does not exceed limits determined in the mooring analysis', '\n\nA line length measuring system shall be available which indicates line lengths in use', ' The system shall be calibrated regularly', ' Additionally, a log shall be available indicating calibration of the line length measuring system, when calibration was last carried out and how the winches have been run', '\n\nIn cases with thruster-assisted mooring the power system shall have sufficient redundancy so that power can be immediately provided following any single failure in any sub-system or component', '\n\nThe power management system shall have adequate response time to power demand changes in both normal operation and fault situations', '\n\nUpon loss of a generator the power management system shall ensure sufficient power on remaining generators avoiding overloading', '\n\nAll computer systems shall be backed up by UPS/battery supplies with at least 30 minutes battery capacity', '\n\nThe thruster system shall have sufficient redundancy such that thrust can be provided following any single failure in any sub-system or component', '\n\nA failure in the thruster control system shall not make the thruster rotate or give increased thrust (especially on variable pitch propellers, variable speed propellers does normally not have the same problem)', '\n \n\n\nFor position keeping systems, the safety factors shall be met in the survival condition for the following failure modes:\n\n\uf0be\tloss of holding power of any-one single thruster;\n\uf0be\tloss of thrust of any one single thruster;\n\uf0be\tsingle failure in thruster control or power system leading to stop of one or several thrusters', '\n\nFor position keeping systems, the unit shall comply with one of the following:\n\n\uf0be\tthe unit is designed for black out of the thruster system,\n\uf0be\tthe system is to include redundant components or systems so that the single failure will not cause critical loss of position or exceedance of anchor line tension, or\n\uf0be\tthe safety factors for intact condition (consequence Class 3) are met in spite of one single failure', ' The system should comply with NMA Regulations No']
288 | 24.4.4.2 Position Reference System | ['For installations with thruster-assisted mooring the positioning reference systems shall supply the positioning mooring system with adequate information whenever the vessel is moored at the location', '\n\nThere shall be a sufficient number of position reference systems (typically one acoustic and one differential GPS-system)', '\n\nIf more than one position reference system is required, they shall be based on at least two different principles', '\n\nMonitoring of position reference systems shall be provided to indicate failures or degraded operation', ' Manual control levers for the thrusters shall be provided in the position mooring control station', '\nIf a vessel is operating in the vicinity of other structures, direct view to the vessel surroundings shall be provided from the positioning mooring control room']
289 | 24.5 Survivability requirements | ['System and components incorporated in systems shall resist design accidental loads to which they may be exposed for the required period of time', '\n\nLocation of vents from tanks and spaces within the hull shall take into account l maximum inclination angles in damaged conditions']
290 | 25 Avoidance of Vessel Collisions | []
291 | 25.1 Role | ['The Vessel Collision Avoidance System shall reduce the risk of vessel collisions']
292 | 25.2 Interfaces | []
293 | 25.3 Required utilities | ['Emergency power supply to keep the collision avoidance systems operational should main power supply fail']
294 | 25.4 Functional requirements | []
295 | 25.4.1 System for detection of vessel or drifting object on collision course. | ['Traffic display for radar and AIS signals shall be available', ' The AIS coverage around the installation shall be sufficient to detect AIS signals from vessels at a minimum of 20 nautical miles', '\n\nThe radar coverage around the installation shall be sufficient to detect an approaching vessel sufficiently early to carry out the necessary emergency response actions, typically 50-70 minutes before collision between the vessel and the offshore unit', '\n\nThe unit responsible for surveillance shall be defined', '\n\nIf radars are installed on the installation, it shall able to register the object’s course and speed, including plotting facilities', '\n\nRadar signals shall be transmitted to the unit responsible for surveillance', '\n\nThe radar shall be provided with a proximity alarm to warn of an approaching vessel with Time to Closest Point of Approach (TCPA)']
296 | 25.4.2 Communication system | ['The communication system shall provide sufficient means for communication between the installation, the remote surveillance centre, and the vessel on collision course', '\n\nThe installation shall be equipped with VHF and GMDSS, ref', '\n\nIf a dedicated standby vessel is used, it shall be equipped with necessary equipment to get attention from vessel on collision course, e', '\n\nIf there is no dedicated standby vessel, the installation shall be equipped with the same equipment normally on the standby vessel', ' It should be noted that a standby vessel may play an important role in\n \n\n\navoiding vessel collision, and therefore this role shall be considered when assessing the need for a dedicated standby vessel', '\n\nA MOB boat dedicated for collision avoidance operations shall have approved maritime VHF', ' It should be noted that a standby vessel may play an important role in\n \n\n\navoiding vessel collision, and therefore this role shall be considered when assessing the need for a dedicated standby vessel']
297 | 25.4.3 Systems for consequence reduction and evacuation | ['The following measures shall be defined in accordance with the safety strategy:\n\n\uf0be\tevacuation:\no\tmeans to ensure safe abandonment for the people on board the installation to the sea for the maximum POB, following a decision to abandon the installation in danger of vessel collision', '\nEmergency preparedness strategies for situations with vessel on collision course shall be established, Figure 6', '\n\nAll activities shall be carried out within XX minutes', '\n\n\nFigure 6 — Time phases for vessel on collision course\n\nThe following time phases should be estimated for the specific unit:\n\n\uf0be\tT1 = Establish contact with the vessel on collision course by radio (VHF, GMDSS (Global Maritime Distress and Safety System));\n\uf0be\tT2 = Other means of audible or visual warning by encountering support vessel (e']
298 | 25.5 Survivability requirements | []
299 | 26 Well integrity | []
300 | 26.1 Role | []
301 | 26.2 Interfaces | []
302 | 26.3 Required utilities | []
303 | 26.4 Functional requirements | ['Well integrity shall be ensured by at least two independent and tested well barriers', '\n\nIn all well activities, the well barriers shall provide means for shutting in the well both during normal operations and in a well control situation to avoid a blowout situation', '\n\nAll barrier elements shall be designed to function when exposed to maximum well pressure, flow, temperature, erosive or corrosive substances like CO2, H2S and sand production during well life, normal operations and well control situations, e', '\n\nAll wells shall have a system for continuous monitoring of tubing pressure and temperature and of A-annulus pressure', ' In gas lift wells there shall be continuous monitoring of the B-annulus', '\n\nWhen selecting gas lift solutions, the risks related to annulus gas release shall be part of the decision process, ref', ' The consequences of loss of main power during drilling and well intervention activities shall be evaluated\n \n\n\nto ensure that critical functions (emergency system consumers) are maintained during the emergency event', '\n\nFunction and equipment required to secure the well to avoid economical losses due to loss of main power, should have essential power supply']
304 | 26.5 Survivability requirements | [' Well barrier elements shall resist the design accidental loads for the required period of time, e', ' BOP/safety head, control panels, hoses and connections, shall be protected against external loads like fire and explosion, dropped objects and other mechanical impact', ' Well barriers shall also be able to handle well kill scenario loads', '\n\nWell kill equipment shall be suitable for operation in a hazardous area zone 2 including protection such as “flame arrester”, overspeed control and “spark arrester”, ref', '\n\nIt shall be possible to shut down BOP/safety head (secondary barrier) from at least two different and well separated locations on the platform other than on the BOP/safety head control unit to ensure one is available during an accidental event (including influence of wind)', ' In addition, for well intervention, the panels for manual control of the master valve and DHSV for the well in question, shall be located such that one is available during an accidental event typically along escape way to mustering point', '\n\nDry XMTs and wellheads shall as a minimum have fire resistance in accordance with NORSOK D-010 references and subclause 5']